## Summary
Wind Turbine Scaling
P_r | 4500000 | W
v_r | 11.7831 | m/s
rho | 1.225 | kg/m^3
c_p_max | 0.44 |  | guess （Borrowed from Enercon E-112/45.114）
New rotor radius | 56.9982 | m
Original rotor radius | 63 | m
Scale factor | 0.90473
Original hub radius | 1.5 | m
New hub radius | 1.3571 | m
Original blade length | 61.5 | m
New blade length | 55.6411 | m
Cp & Ct Curve
cp_max | 0.48892
lambda_optimal | 8.1
Rotor Scaling
Maximum tip speed | 78 | m/s
Rotor radius | 56.9982 | m
Maximum rotational speed | 1.3685 | rad/s
Maximum rpm | 13.0679 | rpm
Maximum c_p | 0.48892
Optimal tip speed ratio | 8.1
v_r | 11.7831 | m/s
Optimal rotor rpm at rated | 15.9902 | rpm
Blade Design
Radial station r | Bending moment M | Design Load | Proof Load | Calculated Bending moment
(m) | (kNm) | (kNm) | (kNm) | (kNm)
1.236 | 8927.45 | 13391.175 | 16203.3218 | 7487.8724
3.709 | 8189.2 | 12283.8 | 14863.398 | 7124.3925
6.182 | 7461.64 | 11192.46 | 13542.8766 | 6639.9601
9.273 | 6572.29 | 9858.435 | 11928.7063 | 6095.637
12.983 | 5588.84 | 8383.26 | 10143.7446 | 5432.0215
16.692 | 4688.21 | 7032.315 | 8509.1012 | 4722.4383
20.401 | 3851.68 | 5777.52 | 6990.7992 | 4035.489
24.111 | 3084.64 | 4626.96 | 5598.6216 | 3376.9301
27.82 | 2392.49 | 3588.735 | 4342.3693 | 2753.1462
31.529 | 1780.32 | 2670.48 | 3231.2808 | 2172.3138
35.239 | 1254.96 | 1882.44 | 2277.7524 | 1641.9051
38.948 | 821.053 | 1231.5795 | 1490.2112 | 1171.1914
42.657 | 479.053 | 718.5795 | 869.4812 | 769.1088
46.367 | 228.599 | 342.8985 | 414.9072 | 440.4273
49.458 | 88.6041 | 132.9061 | 160.8164 | 212.9932
51.931 | 24.6213 | 36.932 | 44.6877 | 100.5733
54.404 | 1.2193 | 1.8289 | 2.213 | 25.5258
55.64 | 7.1025e-06 | 1.0654e-05 | 1.2891e-05 | 2.3328
A Detailed Wind Turbine Blade Cost Model (nrel.gov)
composite material in the spar
material | E(Young's modulus) |  | V(percentage） | ρ（density） |  | unit price
Glass-epoxy (UD*), Vf = 0.5 | 38 | GPa | 0.66667 | 1840 | kg/m³ | 1.87 | $/kg
Carbon fibre-epoxy (UD), Vf = 0.6 | 130 | GPa | 0.33333 | 1500 | kg/m³ | 30 | $/kg
net tensile modulus | 68.6667 | GPa |  | 1726.6667 | kg/m³ | 11.2467 | $/kg
CF Mass and Cost estimates
Station | Airfoil | Radial station r | Proof Load | Chord length | Max rel. thickness | Section depth T | Spar cap width W | Spar cap thickness t | Area moment Ixx | Stress s | Target stress (MPa) CF | a | b | c | Station | Spar cap length L | Spar cap width W | Spar cap thickness t | Volume | Spar cap mass
|  | (m) | (kNm) | (m) | % | (m) | (m) | (mm) | (m^4) | (Pa) | 200 | (m) | (m) | (m) |  | (m) | (m) | (mm) | (m³) | (kg)
2 | NREL 5-MW Circular 1 | 1.236 | 16203.3218 | 3.205 | 1 | 3.205 | 0.534 | 48.825 | 0.12983 | 200000000 |  | 0.534 | -0.85574 | 0.040508 | 2 | 1.236 | 0.534 | 48.825 | 0.032226 | 48.3386
3 | NREL 5-MW Circular 1 | 3.709 | 14863.398 | 3.487 | 1 | 3.487 | 0.534 | 40.8692 | 0.12957 | 200000000 |  | 0.534 | -0.93103 | 0.037158 | 3 | 2.473 | 0.534 | 40.8692 | 0.053971 | 80.9567
4 | NREL 5-MW Circular 2 | 6.182 | 13542.8766 | 3.77 | 1 | 3.77 | 0.534 | 34.2581 | 0.12764 | 200000000 |  | 0.534 | -1.0066 | 0.033857 | 4 | 2.473 | 0.534 | 34.2581 | 0.045241 | 67.861
5 | NREL 5-MW DU 99-W-405 | 9.273 | 11928.7063 | 4.123 | 0.405 | 1.6698 | 0.534 | 73.3293 | 0.049797 | 200000000 |  | 0.534 | -0.44584 | 0.029822 | 5 | 3.091 | 0.534 | 73.3293 | 0.12104 | 181.5554
6 | NREL 5-MW DU 99-W-350 | 12.983 | 10143.7446 | 4.209 | 0.351 | 1.4774 | 0.534 | 71.1411 | 0.037465 | 200000000 |  | 0.534 | -0.39445 | 0.025359 | 6 | 3.71 | 0.534 | 71.1411 | 0.14094 | 211.4108
7 | NREL 5-MW DU 99-W-350 | 16.692 | 8509.1012 | 4.033 | 0.351 | 1.4156 | 0.534 | 61.6534 | 0.030113 | 200000000 |  | 0.534 | -0.37796 | 0.021273 | 7 | 3.709 | 0.534 | 61.6534 | 0.12211 | 183.1667
8 | NREL 5-MW DU 99-W-300 | 20.401 | 6990.7992 | 3.844 | 0.3 | 1.1532 | 0.534 | 63.8263 | 0.020154 | 200000000 |  | 0.534 | -0.3079 | 0.017477 | 8 | 3.709 | 0.534 | 63.8263 | 0.12641 | 189.6222
9 | NREL 5-MW DU 99-W-250 | 24.111 | 5598.6216 | 3.625 | 0.25 | 0.90625 | 0.534 | 68.0703 | 0.012684 | 200000000 |  | 0.534 | -0.24197 | 0.013997 | 9 | 3.71 | 0.534 | 68.0703 | 0.13486 | 202.2851
10 | NREL 5-MW DU 99-W-250 | 27.82 | 4342.3693 | 3.391 | 0.25 | 0.84775 | 0.534 | 55.1317 | 0.0092031 | 200000000 |  | 0.534 | -0.22635 | 0.010856 | 10 | 3.709 | 0.534 | 55.1317 | 0.10919 | 163.7913
11 | NREL 5-MW DU 99-W-210 | 31.529 | 3231.2808 | 3.168 | 0.21 | 0.66528 | 0.534 | 54.3619 | 0.0053743 | 200000000 |  | 0.534 | -0.17763 | 0.0080782 | 11 | 3.709 | 0.534 | 54.3619 | 0.10767 | 161.5042
12 | NREL 5-MW DU 99-W-210 | 35.239 | 2277.7524 | 2.946 | 0.21 | 0.61866 | 0.534 | 39.5232 | 0.0035229 | 200000000 |  | 0.534 | -0.16518 | 0.0056944 | 12 | 3.71 | 0.534 | 39.5232 | 0.078301 | 117.4516
13 | NREL 5-MW NACA64-618 | 38.948 | 1490.2112 | 2.723 | 0.18 | 0.49014 | 0.534 | 32.8791 | 0.001826 | 200000000 |  | 0.534 | -0.13087 | 0.0037255 | 13 | 3.709 | 0.534 | 32.8791 | 0.065121 | 97.6808
14 | NREL 5-MW NACA64-618 | 42.657 | 869.4812 | 2.501 | 0.18 | 0.45018 | 0.534 | 19.8316 | 0.00097856 | 200000000 |  | 0.534 | -0.1202 | 0.0021737 | 14 | 3.709 | 0.534 | 19.8316 | 0.039279 | 58.9179
15 | NREL 5-MW NACA64-618 | 46.367 | 414.9072 | 2.278 | 0.18 | 0.41004 | 0.534 | 9.9581 | 0.00042532 | 200000000 |  | 0.534 | -0.10948 | 0.0010373 | 15 | 3.71 | 0.534 | 9.9581 | 0.019728 | 29.5926
16 | NREL 5-MW NACA64-618 | 49.458 | 160.8164 | 2.096 | 0.18 | 0.37728 | 0.534 | 4.0793 | 0.00015168 | 200000000 |  | 0.534 | -0.10073 | 0.00040204 | 16 | 3.091 | 0.534 | 4.0793 | 0.0067333 | 10.1
17 | NREL 5-MW NACA64-618 | 51.931 | 44.6877 | 1.887 | 0.18 | 0.33966 | 0.534 | 1.241 | 3.7947e-05 | 200000000 |  | 0.534 | -0.090689 | 0.00011172 | 17 | 2.473 | 0.534 | 1.241 | 0.0016388 | 2.4582
18 | NREL 5-MW NACA64-618 | 54.404 | 2.213 | 1.284 | 0.18 | 0.23112 | 0.534 | 0.089725 | 1.2787e-06 | 200000000 |  | 0.534 | -0.061709 | 5.5325e-06 | 18 | 2.473 | 0.534 | 0.089725 | 0.00011849 | 0.17773
19 | NREL 5-MW NACA64-618 | 55.64 | 1.2891e-05 | 1.284 | 0.18 | 0.23112 | 0.534 | 5.2225e-07 | 7.4484e-12 | 200000000 |  | 0.534 | -0.061709 | 3.2228e-11 | 19 | 1.236 | 0.534 | 5.2225e-07 | 3.447e-10 | 5.1705e-07
[19 empty] | total mass | 3613.7415 | kg
[19 empty] | unit price | 30 | $/kg
[19 empty] | cost | 108412.245 | $
[20 empty] | 86729.796 | £ | (1$=0.8£, 13/4/2023 UTC 16:53)
(2/3GF+1/3CF) Mass and Cost estimates
Station | Airfoil | Radial station r | Proof Load | Chord length | Max rel. thickness | Section depth T | Spar cap width W | Spar cap thickness t | Area moment Ixx | Stress s | Target stress (MPa) GF+CF | a | b | c | Station | Spar cap length L | Spar cap width W | Spar cap thickness t | Volume | Spar cap mass
|  | (m) | (kNm) | (m) | % | (m) | (m) | (mm) | (m^4) | (Pa) | 120 | (m) | (m) | (m) |  | (m) | (m) | (mm) | (m³) | (kg)
2 | NREL 5-MW Circular 1 | 1.236 | 16203.3218 | 3.205 | 1 | 3.205 | 0.534 | 83.2172 | 0.21638 | 120000000 |  | 0.534 | -0.85574 | 0.067514 | 2 | 1.236 | 0.534 | 83.2172 | 0.054925 | 94.8377
3 | NREL 5-MW Circular 1 | 3.709 | 14863.398 | 3.487 | 1 | 3.487 | 0.534 | 69.2709 | 0.21595 | 120000000 |  | 0.534 | -0.93103 | 0.061931 | 3 | 2.473 | 0.534 | 69.2709 | 0.091478 | 157.9518
4 | NREL 5-MW Circular 2 | 6.182 | 13542.8766 | 3.77 | 1 | 3.77 | 0.534 | 57.8336 | 0.21274 | 120000000 |  | 0.534 | -1.0066 | 0.056429 | 4 | 2.473 | 0.534 | 57.8336 | 0.076374 | 131.8725
5 | NREL 5-MW DU 99-W-405 | 9.273 | 11928.7063 | 4.123 | 0.405 | 1.6698 | 0.534 | 132.5135 | 0.082995 | 120000000 |  | 0.534 | -0.44584 | 0.049703 | 5 | 3.091 | 0.534 | 132.5135 | 0.21873 | 377.6668
6 | NREL 5-MW DU 99-W-350 | 12.983 | 10143.7446 | 4.209 | 0.351 | 1.4774 | 0.534 | 130.0433 | 0.062441 | 120000000 |  | 0.534 | -0.39445 | 0.042266 | 6 | 3.71 | 0.534 | 130.0433 | 0.25763 | 444.8481
7 | NREL 5-MW DU 99-W-350 | 16.692 | 8509.1012 | 4.033 | 0.351 | 1.4156 | 0.534 | 111.31 | 0.050189 | 120000000 |  | 0.534 | -0.37796 | 0.035455 | 7 | 3.709 | 0.534 | 111.31 | 0.22046 | 380.6631
8 | NREL 5-MW DU 99-W-300 | 20.401 | 6990.7992 | 3.844 | 0.3 | 1.1532 | 0.534 | 119.275 | 0.033591 | 120000000 |  | 0.534 | -0.3079 | 0.029128 | 8 | 3.709 | 0.534 | 119.275 | 0.23624 | 407.9021
9 | NREL 5-MW DU 99-W-250 | 24.111 | 5598.6216 | 3.625 | 0.25 | 0.90625 | 0.534 | 139.1214 | 0.021141 | 120000000 |  | 0.534 | -0.24197 | 0.023328 | 9 | 3.71 | 0.534 | 139.1214 | 0.27562 | 475.9022
10 | NREL 5-MW DU 99-W-250 | 27.82 | 4342.3693 | 3.391 | 0.25 | 0.84775 | 0.534 | 106.8894 | 0.015339 | 120000000 |  | 0.534 | -0.22635 | 0.018093 | 10 | 3.709 | 0.534 | 106.8894 | 0.21171 | 365.5454
11 | NREL 5-MW DU 99-W-210 | 31.529 | 3231.2808 | 3.168 | 0.21 | 0.66528 | 0.534 | 116.8278 | 0.0089571 | 120000000 |  | 0.534 | -0.17763 | 0.013464 | 11 | 3.709 | 0.534 | 116.8278 | 0.23139 | 399.5331
12 | NREL 5-MW DU 99-W-210 | 35.239 | 2277.7524 | 2.946 | 0.21 | 0.61866 | 0.534 | 76.2524 | 0.0058715 | 120000000 |  | 0.534 | -0.16518 | 0.0094906 | 12 | 3.71 | 0.534 | 76.2524 | 0.15107 | 260.8418
13 | NREL 5-MW NACA64-618 | 38.948 | 1490.2112 | 2.723 | 0.18 | 0.49014 | 0.534 | 64.3363 | 0.0030434 | 120000000 |  | 0.534 | -0.13087 | 0.0062092 | 13 | 3.709 | 0.534 | 64.3363 | 0.12742 | 220.0203
14 | NREL 5-MW NACA64-618 | 42.657 | 869.4812 | 2.501 | 0.18 | 0.45018 | 0.534 | 35.8506 | 0.0016309 | 120000000 |  | 0.534 | -0.1202 | 0.0036228 | 14 | 3.709 | 0.534 | 35.8506 | 0.071006 | 122.6034
15 | NREL 5-MW NACA64-618 | 46.367 | 414.9072 | 2.278 | 0.18 | 0.41004 | 0.534 | 17.2405 | 0.00070887 | 120000000 |  | 0.534 | -0.10948 | 0.0017288 | 15 | 3.71 | 0.534 | 17.2405 | 0.034156 | 58.9758
16 | NREL 5-MW NACA64-618 | 49.458 | 160.8164 | 2.096 | 0.18 | 0.37728 | 0.534 | 6.9046 | 0.0002528 | 120000000 |  | 0.534 | -0.10073 | 0.00067007 | 16 | 3.091 | 0.534 | 6.9046 | 0.011397 | 19.6783
17 | NREL 5-MW NACA64-618 | 51.931 | 44.6877 | 1.887 | 0.18 | 0.33966 | 0.534 | 2.0786 | 6.3244e-05 | 120000000 |  | 0.534 | -0.090689 | 0.0001862 | 17 | 2.473 | 0.534 | 2.0786 | 0.0027449 | 4.7396
18 | NREL 5-MW NACA64-618 | 54.404 | 2.213 | 1.284 | 0.18 | 0.23112 | 0.534 | 0.14962 | 2.1311e-06 | 120000000 |  | 0.534 | -0.061709 | 9.2209e-06 | 18 | 2.473 | 0.534 | 0.14962 | 0.00019758 | 0.34116
19 | NREL 5-MW NACA64-618 | 55.64 | 1.2891e-05 | 1.284 | 0.18 | 0.23112 | 0.534 | 8.7042e-07 | 1.2414e-11 | 120000000 |  | 0.534 | -0.061709 | 5.3713e-11 | 19 | 1.236 | 0.534 | 8.7042e-07 | 5.745e-10 | 9.9196e-07
[19 empty] | total mass | 7847.8467 | kg
[19 empty] | unit price | 11.2467 | $/kg
[19 empty] | cost | 88262.1158 | $
[20 empty] | 70609.6927 | £ | (1$=0.8£, 13/4/2023 UTC 16:53)
Tower Design
Tubular Tower Part Info |  |  | Tower Material |  |  | price |  | Price Date | Price in £ |  | cost |  |  | (1¥=0.12£ 13/4/2023 UTC 16:53)
Height | 79.252 | m | Material | Steel |  | 3848 | ¥/t | 21/4/2023 | 461.76 | £/t | 119104.9891 | £ | Commodities - Live Quote Price Trading Data (tradingeconomics.com)
Tower mass | 257.937 | t | E | 210 | GPa
|  |  | Shear modulus | 80.769 | GPa
|  |  | Density | 8500 | kg/m³
|  |  | Yield stress | 355 | Mpa
|  |  | Element Initial length | 4.403 | m
Element | Height(m) | Diameter(m) | Thickness(mm)
1 | 4.403 | 5.375 | 31
2 | 8.806 | 5.268 | 31
3 | 13.209 | 5.161 | 30
4 | 17.612 | 5.054 | 30
5 | 22.015 | 4.946 | 29
6 | 26.418 | 4.839 | 29
7 | 30.821 | 4.732 | 28
8 | 35.224 | 4.625 | 28
9 | 39.627 | 4.518 | 27
10 | 44.03 | 4.411 | 27
11 | 48.433 | 4.304 | 26
12 | 52.836 | 4.197 | 26
13 | 57.239 | 4.09 | 25
14 | 61.642 | 3.983 | 25
15 | 66.045 | 3.876 | 24
16 | 70.448 | 3.769 | 24
17 | 74.851 | 3.662 | 23
18 | 79.254 | 3.555 | 23
Rotational speed | n | 13.0679 | rpm |  | Tower Resonance
Rotational speed |  | 0.2178 | rotations / second |  | 1P (rpm) | 1P (Hz) | 2P (Hz) | 3P (Hz) | Natural frequency 1 | Natural frequency 2 | Natural frequency 3
1P multiplier | 1P | 1 |  |  | 1 | 0.016667 | 0.033333 | 0.05 | 0.34993 | 0.35137 | 0.8032
1P excitation frequency | f_1P | 0.2178 | Hz |  | 2 | 0.033333 | 0.066667 | 0.1 | 0.34993 | 0.35137 | 0.8032
2P multiplier | 2P | 2 |  |  | 3 | 0.05 | 0.1 | 0.15 | 0.34993 | 0.35137 | 0.8032
2P excitation frequency | f_2P | 0.4356 | Hz |  | 4 | 0.066667 | 0.13333 | 0.2 | 0.34993 | 0.35137 | 0.8032
3P multiplier | 3P | 3 |  |  | 5 | 0.083333 | 0.16667 | 0.25 | 0.34993 | 0.35137 | 0.8032
3P excitation frequency | f_3P | 0.65339 | Hz |  | 6 | 0.1 | 0.2 | 0.3 | 0.34993 | 0.35137 | 0.8032
[5 empty] | 7 | 0.11667 | 0.23333 | 0.35 | 0.34993 | 0.35137 | 0.8032
[5 empty] | 8 | 0.13333 | 0.26667 | 0.4 | 0.34993 | 0.35137 | 0.8032
Blade flapwise vibration natural frequency | f_n | 0.34993 | Hz |  | 9 | 0.15 | 0.3 | 0.45 | 0.34993 | 0.35137 | 0.8032
Frequency ratio, 1P | r_1P | 0.6224 | - |  | 10 | 0.16667 | 0.33333 | 0.5 | 0.34993 | 0.35137 | 0.8032
Frequency ratio, 2P | r_2P | 1.2448 | - |  | 11 | 0.18333 | 0.36667 | 0.55 | 0.34993 | 0.35137 | 0.8032
Frequency ratio, 3P | r_3P | 1.8672 | - |  | 12 | 0.2 | 0.4 | 0.6 | 0.34993 | 0.35137 | 0.8032
|  | No damping | Aerodynamic damping |  | 13.0679 | 0.2178 | 0.4356 | 0.65339 | 0.34993 | 0.35137 | 0.8032
|  | ζ=0 | ζ=0.15
0.15
Dynamic magnification factor, 1P | Q_1P | 1.6323 | 1.5614
Dynamic magnification factor, 2P | Q_2P | -1.8197 | 1.5051
Dynamic magnification factor, 3P | Q_3P | -0.40218 | 0.39234
Generator Design
| Direct Drive PMG |  | Comments
Rated power | 4500000 | W | 4.5MW
Gearbox ratio, k | 1 |  | gear ratios 1:1
Generator rotational speed | 13.1 | rpm
Generator rotational speed | 1.3718 | rad/s
Generator rated torque, T | 3280292.7202 | Nm
Generator "radius/axial length" ratio or R/L | 2 |  | Assume Kasp=2
Electromagnetic Shear Stress, σ | 40000 | Pa | Assume 40kPa
Generator radius, R | 2.9664 | m
Generator axial length, L | 1.4832 | m
Generator cylinder surface area, 2πRL | 27.6451 | m2 |  |  |  | (1$=0.8£, 1¥=0.12£ 13/4/2023 UTC 16:53)
Generator volume, V | 41.0037 | m3 |  |  |  | Commodities - Live Quote Price Trading Data (tradingeconomics.com)
[6 empty] | Parameter | Price |  | Price date | Price in £
Iron mass | 26.5458 | ton | Use Surface Area x "Mass/surface area" (from Polinder) |  |  | Iron mass price per tons | 116 | USD/tons | 21/4/2023 | 92.8 | £/tons
Copper mass | 6.3065 | ton |  |  |  | Copper mass price tons | 3.848 | USD/Lbs | 21/4/2023 | 6895.616 | £/tons
Permanent magnet mass | 2.4933 | ton |  |  |  | Neodymium（Permanent magnet） mass price per tons | 605000 | RMB/tons | 21/4/2023 | 72600 | £/tons
Pole pitch guess | 0.1 | m | 0.1m pole pitch is similar to Polinder |  |  | Cost
Poles guess | 186.3864 |  |  |  |  | Iron | 2463.4502 | £
Pole pairs guess | 93.1932 |  |  |  |  | Copper | 43486.9315 | £
[6 empty] | Permanent magnet | 181010.0892 | £
Integer pole pairs | 93 |  | Pole pairs must be integer, so round to nearest |  |  | Total Cost | 226960.471 | £
Integer poles | 186
Pole pitch | 0.10021 | m
Copper loss estimate | 36802.4946 | w | Estimate based on Surface Area x "loss/surface area"
Iron loss estimate | 21999.2816 | w
Total loss estimate | 58801.7763 | w
Foundation Design
wind speed | thrust
m/s | kN
1 | 8.8652
2 | 30.6805
3 | 63.3409
4 | 96.8557
5 | 142.081
6 | 189.701
7 | 244.372
8 | 303.745
9 | 381.828
10 | 469.663
11 | 552.391
11.78 | 606.707
12 | 551.547
13 | 473.571
14 | 417.466
15 | 384.829
16 | 359.695
17 | 321.301
18 | 291.829
19 | 287.38
20 | 279.647
21 | 272.642
22 | 265.366
23 | 255.839
24 | 237.172
25 | 229.837
Rotor mass | 84.61 | t
Nacelle mass | 177.715 | t
Tower mass | 257.937 | t
Total mass | 520.262 | t | weight W of the tower+nacelle+roter |  | 5103770.22 | N
concrete plinth | 1.5 | m
buried depth | 1.8 | m
hub height | 79.252 | m
density of reinforced concrete | 2500 | kg/m3
density of the soil and rock backfill | 2200 | kg/m3
rotor thrust | 606.707 | kN
overturning moment is Mt | 50084.8763 | kNm | Mt=TH
concrete plinth and the overlying soil Mc | 3750 | B² kg
mass of soil Ms | 3960 | B² kg
The total mass of the base Mb | 7710 | B² kg
gravity g | 9.81 | m/s²
weight W of the foundation | 75635.1 | B² N
weight moment Mw | 37817.55 | B³ Nm | Mw=WB/2 | weight moment Mw' | 37817.55 | B³ ＋ | 2551885.11 | B | Nm
B | 15.8384 | m | Mw≥3Mt | B | 14.4224 |  |  |  | m | Mw'≥3Mt
cost
volume | 245.0508 | m³
steel bars needed | 40 | t | assumed
cost list
Concrete C40 price | 115 | £/m³ | Ready Mix Concrete Prices for 2023 ¦ Mister Concrete
steel bars | 461.76 | £/t | Steel price |  | Price Date | Price in £ |  |  | (1¥=0.12£ 13/4/2023 UTC 16:53)
concrete | 28180.8372 | £ | 3848 | ¥/t | 21/4/2023 | 461.76 | £/t | Commodities - Live Quote Price Trading Data (tradingeconomics.com)
steel bars | 18470.4 | £
total | 46651.2372 | £
Energy Yield
"V1" | "V2" | Rayleigh fit at 78.5m | Wind Speed (m) | Power (kW) | P90 Energy (kWh)
0 | 0.5 | 49.2701 | 0 | 0 | 0
0.5 | 1.5 | 384.3145 | 1 | 0 | 0
1.5 | 2.5 | 718.5097 | 2 | 0 | 0
2.5 | 3.5 | 963.2009 | 3 | 41.3979 | 39874.4936
3.5 | 4.5 | 1097.3009 | 4 | 170.099 | 186649.7856
4.5 | 5.5 | 1120.4255 | 5 | 343.608 | 384987.1492
5.5 | 6.5 | 1049.998 | 6 | 641.894 | 673987.3874
6.5 | 7.5 | 914.611 | 7 | 1034.53 | 946192.5262
7.5 | 8.5 | 746.1161 | 8 | 1556.85 | 1161590.8087
8.5 | 9.5 | 572.8141 | 9 | 2209.27 | 1265500.9351
9.5 | 10.5 | 415.2432 | 10 | 3029.67 | 1258049.8637
10.5 | 11.5 | 284.9069 | 11 | 4039.22 | 1150801.8464
11.5 | 12.5 | 185.3428 | 12 | 4841.82 | 897396.5219
12.5 | 13.5 | 114.4717 | 13 | 4909.54 | 562003.3858
13.5 | 14.5 | 67.1922 | 14 | 4854.33 | 326173.2562
14.5 | 15.5 | 37.5141 | 15 | 4894.49 | 183612.2802
15.5 | 16.5 | 19.9347 | 16 | 4846.33 | 96610.3243
16.5 | 17.5 | 10.0879 | 17 | 4864.93 | 49077.1093
17.5 | 18.5 | 4.8637 | 18 | 4981.15 | 24226.6607
18.5 | 19.5 | 2.2349 | 19 | 4968.14 | 11103.2898
19.5 | 20.5 | 0.97909 | 20 | 4867.98 | 4766.1798
20.5 | 21.5 | 0.40905 | 21 | 4898.2 | 2003.5914
21.5 | 22.5 | 0.16301 | 22 | 4978.85 | 811.5976
22.5 | 23.5 | 0.061976 | 23 | 4932.38 | 305.6911
23.5 | 24.5 | 0.022485 | 24 | 4917.32 | 110.5659
24.5 | 25.5 | 0.0077853 | 25 | 4995.86 | 38.8944
25.5 | 26.5 | 0.002573
26.5 | 27.5 | 0.00081177
27.5 | 28.5 | 0.00024451
28.5 | 29.5 | 7.0321e-05 | energy per WT per year |  | 9225874.1443
29.5 | 30.5 | 1.9312e-05 | energy 3 WTs per year |  | 27677622.433
Controller Design
rated wind speed | 11.604 | m/s
K_u | 2.99 | s
T_u | 3.525 | s
K_p(0) | 1.3455 | s
K_I(0) | 0.45804
theta_k | 40 | degrees
Curves
Cost Attemption
WT P_rated | 4500 | kW
Averaged CapEx | 1501 | $/kW |  | 2021 Cost of Wind Energy Review (nrel.gov)
Parameter | Value | Cost | Cost
| $/kW | $ | £
Wind Turbine CapEx | 1030 | 1546030 | 1236824
Rotor | 313 | 469813 | 375850.4
Nacelle | 512 | 768512 | 614809.6
Tower | 204 | 306204 | 244963.2
Bos CapEx | 322 | 483322 | 386657.6
Engineering | 23 | 34523 | 27618.4
Project Management | 10 | 15010 | 12008
Foundation | 75 | 112575 | 90060
Site access, staing, facilities | 40 | 60040 | 48032
Assembly and installation | 41 | 61541 | 49232.8
Electrical infrastructure | 132 | 198132 | 158505.6
Financial CapEx | 113 | 169613 | 135690.4
Construction finance | 23 | 34523 | 27618.4
Contingency | 90 | 135090 | 108072
Total CapEx | 1501 | 2253001 | 1802400.8
(1$=0.8£, 13/4/2023 UTC 16:53)
Annual cost (fixed)
Insurance and taxes | 38000 | £ | tutorial
Electrical O&M | 3000 | £ | tutorial
Management | 8000 | £ | tutorial
Annual costs (variable) |  |  | tutorial
Availability warranty | 13.5705 | £/MWh | scale 15 to factor of 0.9047
Estimated OpEx | 32 | £/kW-yr
Estimated Total OpEx | 144000 | £/yr
Assuming a 20-year lifetime
life time | 20 | year
discount rate | 1.3 | % | https://www.gov.uk/government/publications/dhsc-group-accounting-manual-2021-to-2022/department-of-health-and-social-care-group-accounting-manual-2021-to-2022-additional-guidance-version-1#:~:text=Post%2Demployment%20benefits%20provisions,of%20CPI%20measured%20at%202.90%25.
Annual energy yield | 9225.8741 | MWh
Total capital costs C | 1802400.8 | £
Total fixed costs | 49000 | £
Annual cost per unit output O | 18.8816 | £/MWh
Discounting factor S_n | 17.7396
LCoE | 29.8945 | £/MWh
Maximum Power Output (kW) | Typical Turbine Type | Project Cost |  | actual cost around
100 | Norvento nED100 | 405 | k£ | 279450 | £
800 | Enercon E53 | 1030 | k£ | 710700 | £
1000 | EWT DW61 | 1250 | k£ | 862500 | £
3000 | Enercon E82 | 2330 | k£ | 1607700 | £
3500 | Enercon E126 EP3 | 3130 | k£ | 2159700 | £
estimate for 4500 |  |  |  | 2535728 | £
How much does a wind turbine cost ? - Renewables First
𝑃𝑜𝑙𝑒 𝑝𝑖𝑡𝑐ℎ= 2𝜋𝑅/𝑃𝑜𝑙𝑒𝑠
𝑇=𝜎2𝜋𝑅^2 𝐿
𝑇=𝜎2𝜋𝑅^3 (𝐿/𝑅)
𝑅=∛(𝑇/𝜎2𝜋(𝑅/𝐿))
𝐿𝐶𝑜𝐸=𝐶/(𝑆_𝑛 𝐸)+𝑂
𝑆_𝑛=1+1/𝑟[1−(1+𝑟)^(1−𝑛)]

## Blade design
Station | Airfoil | Radial station r | Proof Load | Chord length | Max rel. thickness | Section depth T | Spar cap width W | Spar cap thickness t | Area moment Ixx | Stress s | Target stress (MPa) GF | a | b | c |  |  | Radial station r | Bending moment M | Design Load | Proof Load | Calculated Bending moment | Simulation Input Data
|  | (m) | (kNm) | (m) | % | (m) | (m) | (mm) | (m^4) | (Pa) | 80 | (m) | (m) | (m) |  |  | (m) | (kNm) | (kNm) | (kNm) | (kNm) | omega | 13.0679 | rpm |  | Hub radius |  | 1.3571 | m
2 | NREL 5-MW Circular 1 | 1.236 | 16203.3218 | 3.205 | 100% | 3.205 | 0.534 | 128.6759 | 0.32457 | 80000000 |  | 0.534 | -0.85574 | 0.10127 |  |  | 1.236 | 8927.45 | 13391.175 | 16203.3218 | 7487.8724 | V | 11 | m/s
3 | NREL 5-MW Circular 1 | 3.709 | 14863.398 | 3.487 | 100% | 3.487 | 0.534 | 106.2534 | 0.32393 | 80000000 |  | 0.534 | -0.93103 | 0.092896 |  |  | 3.709 | 8189.2 | 12283.8 | 14863.398 | 7124.3925 | Air density, ρ | 1.225 | kg/m^3
4 | NREL 5-MW Circular 2 | 6.182 | 13542.8766 | 3.77 | 100% | 3.77 | 0.534 | 88.2174 | 0.3191 | 80000000 |  | 0.534 | -1.0066 | 0.084643 |  |  | 6.182 | 7461.64 | 11192.46 | 13542.8766 | 6639.9601
5 | NREL 5-MW DU 99-W-405 | 9.273 | 11928.7063 | 4.123 | 40.5% | 1.6698 | 0.534 | 231.3016 | 0.12449 | 80000000 |  | 0.534 | -0.44584 | 0.074554 |  |  | 9.273 | 6572.29 | 9858.435 | 11928.7063 | 6095.637 |  |  | Blade Station View |  |  |  |  | Velocity Triangle View |  |  | Sensor Data | [10 empty] | Calculations
6 | NREL 5-MW DU 99-W-350 | 12.983 | 10143.7446 | 4.209 | 35.1% | 1.4774 | 0.534 | 236.3426 | 0.093662 | 80000000 |  | 0.534 | -0.39445 | 0.063398 |  |  | 12.983 | 5588.84 | 8383.26 | 10143.7446 | 5432.0215 | CAD & Sensor View - Blade Station # | Velocity Triangle - Blade Station # | Aerofoil | Chord | Twist Angle, β | Distance to Root | Influence length | Angle of Attack, α | Pitch angle, θ | Axial induction factor, a | Angle of Attack, α | c_D | c_L | Local Wind Speed | Relative Wind Speed | Axial Induction Factor | Induced Velocity | Lift force distributed | Drag force, distributed | Thrust force | Bending Moment | R_mid | dr | c | Ω | U_calc | V | a | (aV)_calc | W_calc | ΔW | ΔW | Inflow Angle, φ_calc | Inflow Angle, φ_calc | Angle of Attack, α_calc | Δα | Δα | (D/dr)_calc | ΔD/dr | ΔD/dr | (L/dr)_calc | ΔL/dr | ΔL/dr | F_res/dr | (F_ax/dr)_calc | Δ(F_ax/dr) | Δ(F_ax/dr) | (F_tan/dr)_calc | Δ(F_tan/dr) | Δ(F_tan/dr) | F_ax |  | r.F_tan |  | Bending Moment
7 | NREL 5-MW DU 99-W-350 | 16.692 | 8509.1012 | 4.033 | 35.1% | 1.4156 | 0.534 | 193.7375 | 0.075283 | 80000000 |  | 0.534 | -0.37796 | 0.053182 |  |  | 16.692 | 4688.21 | 7032.315 | 8509.1012 | 4722.4383 |  |  |  | m | deg | m | m | deg | deg |  | deg | - | - | m/s | m/s |  | m/s | N/m | N/m | N/m | kNm | m | m | m | rad/s | m/s | m/s | - | m/s | m/s | m/s | % | rad | deg | deg | deg | % | N/m | N/m | % | N/m | N/m | % | N/m | N/m | N/m | % | N/m | N/m | % | N |  | Nm |  | Nm
8 | NREL 5-MW DU 99-W-300 | 20.401 | 6990.7992 | 3.844 | 30% | 1.1532 | 0.534 | 252.3036 | 0.050386 | 80000000 |  | 0.534 | -0.3079 | 0.043692 |  |  | 20.401 | 3851.68 | 5777.52 | 6990.7992 | 4035.489 | 2 | 1 | NREL 5-MW Circular 1 | 3.205 | 13.308 | 1.236 | 1.856 | 58.7772 | 0 | 0.1011 | 58.7772 | 0.5 | 0 | 11 | 10.0035 | 0.1011 | 1.1241 | 0 | 98.5261 | 93.1651 | 8927.45 | 2.5931 | 1.856 | 3.205 | 1.3685 | 3.5486 | 11 | 0.1011 | 1.1121 | 10.5054 | 0.50187 | 4.777% | 1.2262 | 70.258 | 56.95 | -1.8272 | -3.208% | 108.3246 | 9.7985 | 9.046% | 0 | 0 |  | 108.3246 | 101.9576 | 8.7925 | 8.624% | -36.5905 | -8964.0405 | 24498% | 189.2333 | 0.09663% | -176.1025 | -0.01664% | 7487872.4453
9 | NREL 5-MW DU 99-W-250 | 24.111 | 5598.6216 | 3.625 | 25% | 0.90625 | 0.534 | #NUM! | 0.031711 | 80000000 |  | 0.534 | -0.24197 | 0.034991 |  |  | 24.111 | 3084.64 | 4626.96 | 5598.6216 | 3376.9301 | 3 | 2 | NREL 5-MW Circular 1 | 3.487 | 13.308 | 3.709 | 2.476 | 44.8547 | 0 | 0.05513 | 44.8547 | 0.5 | 0 | 11 | 11.9612 | 0.05513 | 0.69708 | 0 | 153.182 | 129.223 | 8189.2 | 5.0661 | 2.476 | 3.487 | 1.3685 | 6.9328 | 11 | 0.05513 | 0.60644 | 12.4936 | 0.53238 | 4.261% | 0.98255 | 56.2957 | 42.9877 | -1.867 | -4.343% | 166.687 | 13.505 | 8.102% | 0 | 0 |  | 166.687 | 138.669 | 9.446 | 6.812% | -92.4958 | -8281.6958 | 8954% | 343.3445 | 0.1753% | -1160.2361 | -0.1096% | 7124392.5491
10 | NREL 5-MW DU 99-W-250 | 27.82 | 4342.3693 | 3.391 | 25% | 0.84775 | 0.534 | #NUM! | 0.023008 | 80000000 |  | 0.534 | -0.22635 | 0.02714 |  |  | 27.82 | 2392.49 | 3588.735 | 4342.3693 | 2753.1462 | 4 | 3 | NREL 5-MW Circular 2 | 3.77 | 13.308 | 6.182 | 2.787 | 34.2124 | 0 | 0.030919 | 34.2124 | 0.35 | 0 | 11 | 14.268 | 0.030919 | 0.45429 | 0 | 164.933 | 120.82 | 7461.64 | 7.5391 | 2.787 | 3.77 | 1.3685 | 10.317 | 11 | 0.030919 | 0.34011 | 14.8349 | 0.56687 | 3.821% | 0.80174 | 45.9365 | 32.6285 | -1.5839 | -4.854% | 177.862 | 12.929 | 7.269% | 0 | 0 |  | 177.862 | 127.8063 | 6.9863 | 5.466% | -123.695 | -7585.335 | 6132% | 356.196 | 0.1819% | -2599.0133 | -0.2456% | 6639960.1087
11 | NREL 5-MW DU 99-W-210 | 31.529 | 3231.2808 | 3.168 | 21% | 0.66528 | 0.534 | #NUM! | 0.013436 | 80000000 |  | 0.534 | -0.17763 | 0.020196 |  |  | 31.529 | 1780.32 | 2670.48 | 3231.2808 | 2172.3138 | 5 | 4 | NREL 5-MW DU 99-W-405 | 4.123 | 13.308 | 9.273 | 3.404 | 15.6957 | 0 | 0.23444 | 15.6957 | 0.21726 | 1.6295 | 11 | 17.2029 | 0.23444 | 2.7527 | 1212.69 | 157.133 | 1136.82 | 6572.29 | 10.6301 | 3.404 | 4.123 | 1.3685 | 14.5469 | 11 | 0.23444 | 2.5789 | 16.8086 | -0.39434 | -2.346% | 0.52476 | 30.0663 | 16.7583 | 1.0626 | 6.341% | 155.0094 | -2.1236 | -1.37% | 1162.6115 | -50.0785 | -4.307% | 1172.8995 | 1083.8377 | -52.9823 | -4.888% | 448.3181 | -6123.9719 | -1366% | 3689.3836 | 1.884% | 16222.3288 | 1.533% | 6095637.0375
12 | NREL 5-MW DU 99-W-210 | 35.239 | 2277.7524 | 2.946 | 21% | 0.61866 | 0.534 | #NUM! | 0.0088072 | 80000000 |  | 0.534 | -0.16518 | 0.014236 |  |  | 35.239 | 1254.96 | 1882.44 | 2277.7524 | 1641.9051 | 6 | 5 | NREL 5-MW DU 99-W-350 | 4.209 | 11.48 | 12.983 | 3.71 | 10.7598 | 0 | 0.25018 | 10.7598 | 0.027737 | 1.5028 | 11 | 21.6014 | 0.25018 | 2.9398 | 1803.1 | 30.4406 | 1680.47 | 5588.84 | 14.3401 | 3.71 | 4.209 | 1.3685 | 19.6239 | 11 | 0.25018 | 2.752 | 21.2868 | -0.31461 | -1.478% | 0.39789 | 22.7973 | 11.3173 | 0.55745 | 4.926% | 32.4015 | 1.9609 | 6.052% | 1755.5343 | -47.5657 | -2.709% | 1755.8333 | 1630.9497 | -49.5203 | -3.036% | 650.3489 | -4938.4911 | -759.4% | 6050.8233 | 3.09% | 34599.7168 | 3.269% | 5432021.4934
13 | NREL 5-MW NACA64-618 | 38.948 | 1490.2112 | 2.723 | 18% | 0.49014 | 0.534 | #NUM! | 0.0045651 | 80000000 |  | 0.534 | -0.13087 | 0.0093138 |  |  | 38.948 | 821.053 | 1231.5795 | 1490.2112 | 1171.1914 | 7 | 6 | NREL 5-MW DU 99-W-350 | 4.033 | 10.162 | 16.692 | 3.709 | 8.3775 | 0 | 0.24071 | 8.3775 | 0.013349 | 1.2928 | 11 | 26.0453 | 0.24071 | 2.7816 | 2154.99 | 21.9357 | 2049.32 | 4688.21 | 18.0491 | 3.709 | 4.033 | 1.3685 | 24.6995 | 11 | 0.24071 | 2.6478 | 26.0735 | 0.028167 | 0.108% | 0.32608 | 18.683 | 8.521 | 0.1435 | 1.684% | 22.4168 | 0.48113 | 2.146% | 2170.9835 | 15.9935 | 0.7367% | 2171.0992 | 2063.7647 | 14.4447 | 0.6999% | 674.201 | -4014.009 | -595.4% | 7654.5032 | 3.909% | 45133.789 | 4.265% | 4722438.3461
14 | NREL 5-MW NACA64-618 | 42.657 | 869.4812 | 2.501 | 18% | 0.45018 | 0.534 | 62.6465 | 0.0024464 | 80000000 |  | 0.534 | -0.1202 | 0.0054343 |  |  | 42.657 | 479.053 | 718.5795 | 869.4812 | 769.1088 | 8 | 7 | NREL 5-MW DU 99-W-300 | 3.844 | 9.011 | 20.401 | 3.709 | 6.804 | 0 | 0.23635 | 6.804 | 0.011107 | 1.1624 | 11 | 30.6017 | 0.23635 | 2.6938 | 2460.55 | 24.1264 | 2460.55 | 3851.68 | 21.7581 | 3.709 | 3.844 | 1.3685 | 29.7752 | 11 | 0.23635 | 2.5999 | 30.9374 | 0.33569 | 1.085% | 0.27497 | 15.7547 | 6.7437 | -0.060271 | -0.8937% | 25.0287 | 0.90229 | 3.605% | 2619.4645 | 158.9145 | 6.067% | 2619.5841 | 2527.8542 | 67.3042 | 2.663% | 687.1492 | -3164.5308 | -460.5% | 9375.8111 | 4.787% | 55453.4847 | 5.24% | 4035488.9649
15 | NREL 5-MW NACA64-618 | 46.367 | 414.9072 | 2.278 | 18% | 0.41004 | 0.534 | 27.329 | 0.0010633 | 80000000 |  | 0.534 | -0.10948 | 0.0025932 |  |  | 46.367 | 228.599 | 342.8985 | 414.9072 | 440.4273 | 9 | 8 | NREL 5-MW DU 99-W-250 | 3.625 | 7.795 | 24.111 | 3.709 | 5.6758 | 0 | 0.24931 | 5.6758 | 0.0094999 | 1.1242 | 11 | 35.233 | 0.24931 | 2.813 | 3087.69 | 25.6891 | 3008.59 | 3084.64 | 25.4681 | 3.709 | 3.625 | 1.3685 | 34.8522 | 11 | 0.24931 | 2.7424 | 35.817 | 0.58404 | 1.631% | 0.23264 | 13.3294 | 5.5344 | -0.14143 | -2.555% | 27.059 | 1.3699 | 5.063% | 3202.2581 | 114.5681 | 3.578% | 3202.3724 | 3122.2305 | 113.6405 | 3.64% | 711.9451 | -2372.6949 | -333.3% | 11580.353 | 5.913% | 67251.182 | 6.354% | 3376930.1361
16 | NREL 5-MW NACA64-618 | 49.458 | 160.8164 | 2.096 | 18% | 0.37728 | 0.534 | 10.5701 | 0.00037921 | 80000000 |  | 0.534 | -0.10073 | 0.0010051 |  |  | 49.458 | 88.6041 | 132.9061 | 160.8164 | 212.9932 | 10 | 9 | NREL 5-MW DU 99-W-250 | 3.391 | 6.544 | 27.82 | 3.709 | 5.233 | 0 | 0.25526 | 5.233 | 0.0086443 | 1.0826 | 11 | 39.9335 | 0.25526 | 2.8622 | 3573.26 | 28.1837 | 3503.63 | 2392.49 | 29.1771 | 3.709 | 3.391 | 1.3685 | 39.9278 | 11 | 0.25526 | 2.8078 | 40.7595 | 0.82603 | 2.027% | 0.20237 | 11.5947 | 5.0507 | -0.18226 | -3.609% | 29.8278 | 1.6441 | 5.512% | 3735.6342 | 162.3742 | 4.347% | 3735.7533 | 3665.3993 | 161.7693 | 4.413% | 721.5961 | -1670.8939 | -231.6% | 13594.9659 | 6.942% | 78089.5897 | 7.379% | 2753146.1908
17 | NREL 5-MW NACA64-618 | 51.931 | 44.6877 | 1.887 | 18% | 0.33966 | 0.534 | 3.1377 | 9.4866e-05 | 80000000 |  | 0.534 | -0.090689 | 0.0002793 |  |  | 51.931 | 24.6213 | 36.932 | 44.6877 | 100.5733 | 11 | 10 | NREL 5-MW DU 99-W-210 | 3.168 | 5.361 | 31.529 | 3.709 | 4.9206 | 0 | 0.27242 | 4.9206 | 0.0088202 | 1.0856 | 11 | 44.6663 | 0.27242 | 3.0397 | 4190.33 | 33.7462 | 4128.29 | 1780.32 | 32.8861 | 3.709 | 3.168 | 1.3685 | 45.0034 | 11 | 0.27242 | 2.9966 | 45.7095 | 1.0432 | 2.282% | 0.176 | 10.084 | 4.723 | -0.19759 | -4.184% | 35.7589 | 2.0127 | 5.629% | 4401.0755 | 210.7455 | 4.788% | 4401.2207 | 4339.3487 | 211.0587 | 4.864% | 735.3892 | -1044.9308 | -142.1% | 16094.6442 | 8.218% | 89698.7656 | 8.476% | 2172313.7748
18 | NREL 5-MW NACA64-618 | 54.404 | 2.213 | 1.284 | 18% | 0.23112 | 0.534 | 0.22457 | 3.1967e-06 | 80000000 |  | 0.534 | -0.061709 | 1.3831e-05 |  |  | 54.404 | 1.2193 | 1.8289 | 2.213 | 25.5258 | 12 | 11 | NREL 5-MW DU 99-W-210 | 2.946 | 4.188 | 35.239 | 3.709 | 4.938 | 0 | 0.28544 | 4.938 | 0.0088549 | 1.0877 | 11 | 49.4326 | 0.28544 | 3.1745 | 4782.94 | 38.6244 | 4725.84 | 1254.96 | 36.5961 | 3.709 | 2.946 | 1.3685 | 50.0804 | 11 | 0.28544 | 3.1399 | 50.6935 | 1.2609 | 2.487% | 0.15568 | 8.9198 | 4.7318 | -0.20624 | -4.359% | 41.0609 | 2.4365 | 5.934% | 5043.5499 | 260.6099 | 5.167% | 5043.717 | 4988.9215 | 263.0815 | 5.273% | 741.4471 | -513.5129 | -69.26% | 18503.9097 | 9.448% | 100640.276 | 9.509% | 1641905.0872
19 | NREL 5-MW NACA64-618 | 55.64 | 1.2891e-05 | 1.284 | 18% | 0.23112 | 0.534 | 1.3056e-06 | 1.8621e-11 | 80000000 |  | 0.534 | -0.061709 | 8.0569e-11 |  |  | 55.64 | 7.1025e-06 | 1.0654e-05 | 1.2891e-05 | 2.3328 | 13 | 12 | NREL 5-MW NACA64-618 | 2.723 | 3.125 | 38.948 | 3.709 | 5.3374 | 0 | 0.27355 | 5.3374 | 0.006847 | 1.0397 | 11 | 54.2407 | 0.27355 | 3.0378 | 5092.56 | 33.0787 | 5035.27 | 821.053 | 40.3051 | 3.709 | 2.723 | 1.3685 | 55.156 | 11 | 0.27355 | 3.0091 | 55.7319 | 1.4912 | 2.676% | 0.14388 | 8.2435 | 5.1185 | -0.21884 | -4.275% | 35.4698 | 2.3911 | 6.741% | 5386.245 | 293.685 | 5.452% | 5386.3618 | 5335.6775 | 300.4075 | 5.63% | 737.1829 | -83.8701 | -11.38% | 19790.0279 | 10.11% | 110202.6708 | 10.41% | 1171191.4349
[22 empty] | 14 | 13 | NREL 5-MW NACA64-618 | 2.501 | 2.319 | 42.657 | 3.709 | 5.3786 | 0 | 0.28096 | 5.3786 | 0.0069607 | 1.0441 | 11 | 59.0425 | 0.28096 | 3.1144 | 5566.53 | 36.6478 | 5507.55 | 479.053 | 44.0141 | 3.709 | 2.501 | 1.3685 | 60.2317 | 11 | 0.28096 | 3.0906 | 60.7488 | 1.7063 | 2.809% | 0.13057 | 7.4811 | 5.1621 | -0.21654 | -4.195% | 39.3502 | 2.7024 | 6.868% | 5902.4564 | 335.9264 | 5.691% | 5902.5875 | 5857.3375 | 349.7875 | 5.972% | 729.4775 | 250.4245 | 34.33% | 21724.8647 | 11.09% | 119085.9618 | 11.25% | 769108.7835
[22 empty] | 15 | 14 | NREL 5-MW NACA64-618 | 2.278 | 1.526 | 46.367 | 3.4 | 5.4601 | 0 | 0.29418 | 5.4601 | 0.0072172 | 1.0519 | 11 | 63.8475 | 0.29418 | 3.2559 | 5977.1 | 40.5679 | 5916.07 | 228.599 | 47.7241 | 3.4 | 2.278 | 1.3685 | 65.3087 | 11 | 0.29418 | 3.2359 | 65.7686 | 1.9211 | 2.921% | 0.11833 | 6.7796 | 5.2536 | -0.20644 | -3.929% | 43.5578 | 2.9899 | 6.864% | 6348.6181 | 371.5181 | 5.852% | 6348.7675 | 6309.3675 | 393.2975 | 6.234% | 706.2083 | 477.6093 | 67.63% | 21451.8496 | 10.95% | 114590.7271 | 10.83% | 440427.3456
[22 empty] | 16 | 15 | NREL 5-MW NACA64-618 | 2.096 | 0.863 | 49.458 | 2.474 | 5.4665 | 0 | 0.3193 | 5.4665 | 0.007249 | 1.0527 | 11 | 67.8485 | 0.3193 | 3.5295 | 6206.46 | 42.3169 | 6146.15 | 88.6041 | 50.8151 | 2.474 | 2.096 | 1.3685 | 69.5386 | 11 | 0.3193 | 3.5123 | 69.9406 | 2.0921 | 2.991% | 0.10726 | 6.1457 | 5.2827 | -0.1838 | -3.479% | 45.5235 | 3.2066 | 7.044% | 6610.8308 | 404.3708 | 6.117% | 6610.9875 | 6577.7107 | 431.5607 | 6.561% | 662.4787 | 573.8746 | 86.63% | 16273.2563 | 8.309% | 83284.5432 | 7.869% | 212993.1826
Station | Airfoil | Radial station r | Proof Load | Chord length | Max rel. thickness | Section depth T | Spar cap width W | Spar cap thickness t | Area moment Ixx | Stress s | Target stress (MPa) CF | a | b | c | [7 empty] | 17 | 16 | NREL 5-MW NACA64-618 | 1.887 | 0.37 | 51.931 | 2.573 | 5.421 | 0 | 0.35819 | 5.421 | 0.0071191 | 1.0482 | 11 | 71.0257 | 0.35819 | 3.9558 | 6112.45 | 41.1056 | 6056.6 | 24.6213 | 53.2881 | 2.573 | 1.887 | 1.3685 | 72.9228 | 11 | 0.35819 | 3.9401 | 73.2638 | 2.2381 | 3.055% | 0.096512 | 5.5297 | 5.1597 | -0.26126 | -5.063% | 44.1651 | 3.0595 | 6.927% | 6502.6147 | 390.1647 | 6% | 6502.7647 | 6476.6094 | 420.0094 | 6.485% | 582.6485 | 558.0272 | 95.77% | 16664.3161 | 8.509% | 79887.1011 | 7.548% | 100573.2588
|  | (m) | (kNm) | (m) | % | (m) | (m) | (mm) | (m^4) | (Pa) | 200 | (m) | (m) | (m) | [7 empty] | 18 | 17 | NREL 5-MW NACA64-618 | 1.284 | 0.106 | 54.404 | 1.855 | 5.1494 | 0 | 0.38652 | 5.1494 | 0.0064298 | 1.0229 | 11 | 74.236 | 0.38652 | 4.2652 | 4431.52 | 27.5932 | 4394.33 | 1.2193 | 55.7611 | 1.855 | 1.284 | 1.3685 | 76.307 | 11 | 0.38652 | 4.2517 | 76.6048 | 2.3688 | 3.092% | 0.088206 | 5.0538 | 4.9478 | -0.20151 | -4.073% | 29.6742 | 2.081 | 7.013% | 4720.9951 | 289.4751 | 6.132% | 4721.0884 | 4705.2556 | 310.9256 | 6.608% | 386.3229 | 385.1036 | 99.68% | 8728.2491 | 4.457% | 39960.0174 | 3.776% | 25525.8089
2 | NREL 5-MW Circular 1 | 1.236 | 16203.3218 | 3.205 | 100% | 3.205 | 0.534 | 48.825 | 0.12983 | 200000000 |  | 0.534 | -0.85574 | 0.040508 | [7 empty] | 19 | 18 | NREL 5-MW NACA64-618 | 1.284 | 0.106 | 55.64 | 0.618 | 8.0951 | 0 | 0 | 8.0951 | 0.012552 | 1.2623 | 11 | 75.9794 | 0 | 0 | 0 | 0 | 0 | 7.1025e-06 | 56.9971 | 0.618 | 1.284 | 1.3685 | 77.9984 | 11 | 0 | 0 | 78.7703 | 2.7909 | 3.543% | 0.1401 | 8.0274 | 7.9214 | -0.17365 | -2.192% | 61.2494 | 61.2494 | 100% | 6159.781 | 6159.781 | 100% | 6160.0855 | 6107.9771 | 6107.9771 | 100% | 799.5432 | 799.5432 | 100% | 3774.7298 | 1.927% | 28163.2756 | 2.661% | 2332.783
3 | NREL 5-MW Circular 1 | 3.709 | 14863.398 | 3.487 | 100% | 3.487 | 0.534 | 40.8692 | 0.12957 | 200000000 |  | 0.534 | -0.93103 | 0.037158
4 | NREL 5-MW Circular 2 | 6.182 | 13542.8766 | 3.77 | 100% | 3.77 | 0.534 | 34.2581 | 0.12764 | 200000000 |  | 0.534 | -1.0066 | 0.033857 | [56 empty] | 1 blade | 195840.4613 | N | 1058328.0778 | Nm
5 | NREL 5-MW DU 99-W-405 | 9.273 | 11928.7063 | 4.123 | 40.5% | 1.6698 | 0.534 | 73.3293 | 0.049797 | 200000000 |  | 0.534 | -0.44584 | 0.029822 | [56 empty] | 3 blades | 587521.3839 | N | 3174984.2335 | Nm
6 | NREL 5-MW DU 99-W-350 | 12.983 | 10143.7446 | 4.209 | 35.1% | 1.4774 | 0.534 | 71.1411 | 0.037465 | 200000000 |  | 0.534 | -0.39445 | 0.025359
7 | NREL 5-MW DU 99-W-350 | 16.692 | 8509.1012 | 4.033 | 35.1% | 1.4156 | 0.534 | 61.6534 | 0.030113 | 200000000 |  | 0.534 | -0.37796 | 0.021273
8 | NREL 5-MW DU 99-W-300 | 20.401 | 6990.7992 | 3.844 | 30% | 1.1532 | 0.534 | 63.8263 | 0.020154 | 200000000 |  | 0.534 | -0.3079 | 0.017477
9 | NREL 5-MW DU 99-W-250 | 24.111 | 5598.6216 | 3.625 | 25% | 0.90625 | 0.534 | 68.0703 | 0.012684 | 200000000 |  | 0.534 | -0.24197 | 0.013997
10 | NREL 5-MW DU 99-W-250 | 27.82 | 4342.3693 | 3.391 | 25% | 0.84775 | 0.534 | 55.1317 | 0.0092031 | 200000000 |  | 0.534 | -0.22635 | 0.010856
11 | NREL 5-MW DU 99-W-210 | 31.529 | 3231.2808 | 3.168 | 21% | 0.66528 | 0.534 | 54.3619 | 0.0053743 | 200000000 |  | 0.534 | -0.17763 | 0.0080782
12 | NREL 5-MW DU 99-W-210 | 35.239 | 2277.7524 | 2.946 | 21% | 0.61866 | 0.534 | 39.5232 | 0.0035229 | 200000000 |  | 0.534 | -0.16518 | 0.0056944
13 | NREL 5-MW NACA64-618 | 38.948 | 1490.2112 | 2.723 | 18% | 0.49014 | 0.534 | 32.8791 | 0.001826 | 200000000 |  | 0.534 | -0.13087 | 0.0037255
14 | NREL 5-MW NACA64-618 | 42.657 | 869.4812 | 2.501 | 18% | 0.45018 | 0.534 | 19.8316 | 0.00097856 | 200000000 |  | 0.534 | -0.1202 | 0.0021737
15 | NREL 5-MW NACA64-618 | 46.367 | 414.9072 | 2.278 | 18% | 0.41004 | 0.534 | 9.9581 | 0.00042532 | 200000000 |  | 0.534 | -0.10948 | 0.0010373
16 | NREL 5-MW NACA64-618 | 49.458 | 160.8164 | 2.096 | 18% | 0.37728 | 0.534 | 4.0793 | 0.00015168 | 200000000 |  | 0.534 | -0.10073 | 0.00040204
17 | NREL 5-MW NACA64-618 | 51.931 | 44.6877 | 1.887 | 18% | 0.33966 | 0.534 | 1.241 | 3.7947e-05 | 200000000 |  | 0.534 | -0.090689 | 0.00011172
18 | NREL 5-MW NACA64-618 | 54.404 | 2.213 | 1.284 | 18% | 0.23112 | 0.534 | 0.089725 | 1.2787e-06 | 200000000 |  | 0.534 | -0.061709 | 5.5325e-06
19 | NREL 5-MW NACA64-618 | 55.64 | 1.2891e-05 | 1.284 | 18% | 0.23112 | 0.534 | 5.2225e-07 | 7.4484e-12 | 200000000 |  | 0.534 | -0.061709 | 3.2228e-11
Station | Airfoil | Radial station r | Proof Load | Chord length | Max rel. thickness | Section depth T | Spar cap width W | Spar cap thickness t | Area moment Ixx | Stress s | Target stress (MPa) GF+CF | a | b | c
|  | (m) | (kNm) | (m) | % | (m) | (m) | (mm) | (m^4) | (Pa) | 120 | (m) | (m) | (m)
2 | NREL 5-MW Circular 1 | 1.236 | 16203.3218 | 3.205 | 100% | 3.205 | 0.534 | 83.2172 | 0.21638 | 120000000 |  | 0.534 | -0.85574 | 0.067514
3 | NREL 5-MW Circular 1 | 3.709 | 14863.398 | 3.487 | 100% | 3.487 | 0.534 | 69.2709 | 0.21595 | 120000000 |  | 0.534 | -0.93103 | 0.061931
4 | NREL 5-MW Circular 2 | 6.182 | 13542.8766 | 3.77 | 100% | 3.77 | 0.534 | 57.8336 | 0.21274 | 120000000 |  | 0.534 | -1.0066 | 0.056429
5 | NREL 5-MW DU 99-W-405 | 9.273 | 11928.7063 | 4.123 | 40.5% | 1.6698 | 0.534 | 132.5135 | 0.082995 | 120000000 |  | 0.534 | -0.44584 | 0.049703
6 | NREL 5-MW DU 99-W-350 | 12.983 | 10143.7446 | 4.209 | 35.1% | 1.4774 | 0.534 | 130.0433 | 0.062441 | 120000000 |  | 0.534 | -0.39445 | 0.042266
7 | NREL 5-MW DU 99-W-350 | 16.692 | 8509.1012 | 4.033 | 35.1% | 1.4156 | 0.534 | 111.31 | 0.050189 | 120000000 |  | 0.534 | -0.37796 | 0.035455
8 | NREL 5-MW DU 99-W-300 | 20.401 | 6990.7992 | 3.844 | 30% | 1.1532 | 0.534 | 119.275 | 0.033591 | 120000000 |  | 0.534 | -0.3079 | 0.029128
9 | NREL 5-MW DU 99-W-250 | 24.111 | 5598.6216 | 3.625 | 25% | 0.90625 | 0.534 | 139.1214 | 0.021141 | 120000000 |  | 0.534 | -0.24197 | 0.023328
10 | NREL 5-MW DU 99-W-250 | 27.82 | 4342.3693 | 3.391 | 25% | 0.84775 | 0.534 | 106.8894 | 0.015339 | 120000000 |  | 0.534 | -0.22635 | 0.018093
11 | NREL 5-MW DU 99-W-210 | 31.529 | 3231.2808 | 3.168 | 21% | 0.66528 | 0.534 | 116.8278 | 0.0089571 | 120000000 |  | 0.534 | -0.17763 | 0.013464
12 | NREL 5-MW DU 99-W-210 | 35.239 | 2277.7524 | 2.946 | 21% | 0.61866 | 0.534 | 76.2524 | 0.0058715 | 120000000 |  | 0.534 | -0.16518 | 0.0094906
13 | NREL 5-MW NACA64-618 | 38.948 | 1490.2112 | 2.723 | 18% | 0.49014 | 0.534 | 64.3363 | 0.0030434 | 120000000 |  | 0.534 | -0.13087 | 0.0062092
14 | NREL 5-MW NACA64-618 | 42.657 | 869.4812 | 2.501 | 18% | 0.45018 | 0.534 | 35.8506 | 0.0016309 | 120000000 |  | 0.534 | -0.1202 | 0.0036228
15 | NREL 5-MW NACA64-618 | 46.367 | 414.9072 | 2.278 | 18% | 0.41004 | 0.534 | 17.2405 | 0.00070887 | 120000000 |  | 0.534 | -0.10948 | 0.0017288
16 | NREL 5-MW NACA64-618 | 49.458 | 160.8164 | 2.096 | 18% | 0.37728 | 0.534 | 6.9046 | 0.0002528 | 120000000 |  | 0.534 | -0.10073 | 0.00067007
17 | NREL 5-MW NACA64-618 | 51.931 | 44.6877 | 1.887 | 18% | 0.33966 | 0.534 | 2.0786 | 6.3244e-05 | 120000000 |  | 0.534 | -0.090689 | 0.0001862
18 | NREL 5-MW NACA64-618 | 54.404 | 2.213 | 1.284 | 18% | 0.23112 | 0.534 | 0.14962 | 2.1311e-06 | 120000000 |  | 0.534 | -0.061709 | 9.2209e-06
19 | NREL 5-MW NACA64-618 | 55.64 | 1.2891e-05 | 1.284 | 18% | 0.23112 | 0.534 | 8.7042e-07 | 1.2414e-11 | 120000000 |  | 0.534 | -0.061709 | 5.3713e-11
composite material in the spar
material | E(Young's modulus) |  | V(percentage） | ρ（density） |  | unit price
Glass-epoxy (UD*), Vf = 0.5 | 38 | GPa | 0.66667 | 1840 | kg/m³ | 1.87 | $/kg
Carbon fibre-epoxy (UD), Vf = 0.6 | 130 | GPa | 0.33333 | 1500 | kg/m³ | 30 | $/kg
net tensile modulus | 68.6667 | GPa |  | 1726.6667 | kg/m³ | 11.2467 | $/kg
GF Mass and Cost estimates | [6 empty] | CF Mass and Cost estimates | [6 empty] | (2/3GF+1/3CF) Mass and Cost estimates
Station | Spar cap length L | Spar cap width W | Spar cap thickness t | Volume | Spar cap mass |  | Station | Spar cap length L | Spar cap width W | Spar cap thickness t | Volume | Spar cap mass |  | Station | Spar cap length L | Spar cap width W | Spar cap thickness t | Volume | Spar cap mass
| (m) | (m) | (mm) | (m³) | (kg) |  |  | (m) | (m) | (mm) | (m³) | (kg) |  |  | (m) | (m) | (mm) | (m³) | (kg)
2 | 1.236 | 0.534 | 128.6759 | 0.084929 | 156.2697 |  | 2 | 1.236 | 0.534 | 48.825 | 0.032226 | 48.3386 |  | 2 | 1.236 | 0.534 | 83.2172 | 0.054925 | 94.8377
3 | 2.473 | 0.534 | 106.2534 | 0.14032 | 258.182 |  | 3 | 2.473 | 0.534 | 40.8692 | 0.053971 | 80.9567 |  | 3 | 2.473 | 0.534 | 69.2709 | 0.091478 | 157.9518
4 | 6.182 | 0.534 | 88.2174 | 0.29122 | 535.8488 |  | 4 | 2.473 | 0.534 | 34.2581 | 0.045241 | 67.861 |  | 4 | 2.473 | 0.534 | 57.8336 | 0.076374 | 131.8725
5 | 3.091 | 0.534 | 231.3016 | 0.38179 | 702.4844 |  | 5 | 3.091 | 0.534 | 73.3293 | 0.12104 | 181.5554 |  | 5 | 3.091 | 0.534 | 132.5135 | 0.21873 | 377.6668
6 | 12.983 | 0.534 | 236.3426 | 1.6385 | 3014.9221 |  | 6 | 3.71 | 0.534 | 71.1411 | 0.14094 | 211.4108 |  | 6 | 3.71 | 0.534 | 130.0433 | 0.25763 | 444.8481
7 | 3.709 | 0.534 | 193.7375 | 0.38372 | 706.0405 |  | 7 | 3.709 | 0.534 | 61.6534 | 0.12211 | 183.1667 |  | 7 | 3.709 | 0.534 | 111.31 | 0.22046 | 380.6631
8 | 20.401 | 0.534 | 252.3036 | 2.7486 | 5057.4785 |  | 8 | 3.709 | 0.534 | 63.8263 | 0.12641 | 189.6222 |  | 8 | 3.709 | 0.534 | 119.275 | 0.23624 | 407.9021
9 | 3.71 | 0.534 | #NUM! | #NUM! | #NUM! |  | 9 | 3.71 | 0.534 | 68.0703 | 0.13486 | 202.2851 |  | 9 | 3.71 | 0.534 | 139.1214 | 0.27562 | 475.9022
10 | 27.82 | 0.534 | #NUM! | #NUM! | #NUM! |  | 10 | 3.709 | 0.534 | 55.1317 | 0.10919 | 163.7913 |  | 10 | 3.709 | 0.534 | 106.8894 | 0.21171 | 365.5454
11 | 3.709 | 0.534 | #NUM! | #NUM! | #NUM! |  | 11 | 3.709 | 0.534 | 54.3619 | 0.10767 | 161.5042 |  | 11 | 3.709 | 0.534 | 116.8278 | 0.23139 | 399.5331
12 | 35.239 | 0.534 | #NUM! | #NUM! | #NUM! |  | 12 | 3.71 | 0.534 | 39.5232 | 0.078301 | 117.4516 |  | 12 | 3.71 | 0.534 | 76.2524 | 0.15107 | 260.8418
13 | 3.709 | 0.534 | #NUM! | #NUM! | #NUM! |  | 13 | 3.709 | 0.534 | 32.8791 | 0.065121 | 97.6808 |  | 13 | 3.709 | 0.534 | 64.3363 | 0.12742 | 220.0203
14 | 42.657 | 0.534 | 62.6465 | 1.427 | 2625.7047 |  | 14 | 3.709 | 0.534 | 19.8316 | 0.039279 | 58.9179 |  | 14 | 3.709 | 0.534 | 35.8506 | 0.071006 | 122.6034
15 | 3.71 | 0.534 | 27.329 | 0.054143 | 99.6225 |  | 15 | 3.71 | 0.534 | 9.9581 | 0.019728 | 29.5926 |  | 15 | 3.71 | 0.534 | 17.2405 | 0.034156 | 58.9758
16 | 49.458 | 0.534 | 10.5701 | 0.27916 | 513.6583 |  | 16 | 3.091 | 0.534 | 4.0793 | 0.0067333 | 10.1 |  | 16 | 3.091 | 0.534 | 6.9046 | 0.011397 | 19.6783
17 | 2.473 | 0.534 | 3.1377 | 0.0041436 | 7.6242 |  | 17 | 2.473 | 0.534 | 1.241 | 0.0016388 | 2.4582 |  | 17 | 2.473 | 0.534 | 2.0786 | 0.0027449 | 4.7396
18 | 54.404 | 0.534 | 0.22457 | 0.0065243 | 12.0047 |  | 18 | 2.473 | 0.534 | 0.089725 | 0.00011849 | 0.17773 |  | 18 | 2.473 | 0.534 | 0.14962 | 0.00019758 | 0.34116
19 | 1.236 | 0.534 | 1.3056e-06 | 8.6174e-10 | 1.5856e-06 |  | 19 | 1.236 | 0.534 | 5.2225e-07 | 3.447e-10 | 5.1705e-07 |  | 19 | 1.236 | 0.534 | 8.7042e-07 | 5.745e-10 | 9.9196e-07
|  |  |  | total mass | #NUM! | kg |  |  |  |  | total mass | 3613.7415 | kg |  |  |  |  | total mass | 7847.8467 | kg
(1$=0.8£, 13/4/2023 UTC 16:53) |  |  |  | unit price | 1.87 | $/kg |  |  |  |  | unit price | 30 | $/kg |  |  |  |  | unit price | 11.2467 | $/kg
|  |  |  | cost | #NUM! | $ |  |  |  |  | cost | 108412.245 | $ |  |  |  |  | cost | 88262.1158 | $
[5 empty] | #NUM! | £ | [5 empty] | 86729.796 | £ | [5 empty] | 70609.6927 | £
Reference
blade | length | material cost $ | blade cost $
WindPACT Blade | 33.25 | 24577.65 | 52146.09
IEA Wind Task 37 Land-Based Reference Wind Turbine Blade | 75 | 73638.82 | 154090.4
SNL-100-03 | 100 | 327375.64 | 547723.35
Note on AB6: Alasdair McDonald: This is data that can be found from by right clicking on a blade station
Note on AD7: Alasdair McDonald: In Ashes, twist angle is called "beta". Inflow angle is equal to angle of attack, plus twist angle plus pitch angle
Note on AE7: Alasdair McDonald: Distance to root is defined in Ashes as the distance of the middle of this blade station to the outside of the hub. The hub itself has a radius, so we'll need to add these together to get the radius of the middle of this blade station.
Note on AF7: Alasdair McDonald: In Ashes this is the radial dimension of the blade station, i.e. if a blade station went from Xm to Ym, the influence length would be (Y-X)m
Note on AG7: Alasdair McDonald: This is the inflow angle minus the twist angle minus the pitch angle
Note on AH7: Alasdair McDonald: This is the angle that the whole blade is turned by

## Tower design
Tubular Tower Part Info |  |  | Tower Material |  |  | price |  | Price Date | Price in £ |  | cost |  |  | (1¥=0.12£ 13/4/2023 UTC 16:53)
Height | 79.252 | m | Material | Steel |  | 3848 | ¥/t | 21/4/2023 | 461.76 | £/t | 119104.9891 | £ | Commodities - Live Quote Price Trading Data (tradingeconomics.com)
Tower mass | 257.937 | t | E | 210 | GPa
|  |  | Shear modulus | 80.769 | GPa
|  |  | Density | 8500 | kg/m³
|  |  | Yield stress | 355 | Mpa
|  |  | Element Initial length | 4.403 | m
Element | Height(m) | Diameter(m) | Thickness(mm)
1 | 4.403 | 5.375 | 31
2 | 8.806 | 5.268 | 31
3 | 13.209 | 5.161 | 30
4 | 17.612 | 5.054 | 30
5 | 22.015 | 4.946 | 29
6 | 26.418 | 4.839 | 29
7 | 30.821 | 4.732 | 28
8 | 35.224 | 4.625 | 28
9 | 39.627 | 4.518 | 27
10 | 44.03 | 4.411 | 27
11 | 48.433 | 4.304 | 26
12 | 52.836 | 4.197 | 26
13 | 57.239 | 4.09 | 25
14 | 61.642 | 3.983 | 25
15 | 66.045 | 3.876 | 24
16 | 70.448 | 3.769 | 24
17 | 74.851 | 3.662 | 23
18 | 79.254 | 3.555 | 23
Rotational speed | n | 13.0679 | rpm | [5 empty] | Tower Resonance
Rotational speed |  | 0.2178 | rotations / second | [5 empty] | 1P (rpm) | 1P (Hz) | 2P (Hz) | 3P (Hz) | Natural frequency 1 | Natural frequency 2 | Natural frequency 3
1P multiplier | 1P | 1 | [6 empty] | 1 | 0.016667 | 0.033333 | 0.05 | 0.34993 | 0.35137 | 0.8032
1P excitation frequency | f_1P | 0.2178 | Hz | [5 empty] | 2 | 0.033333 | 0.066667 | 0.1 | 0.34993 | 0.35137 | 0.8032
2P multiplier | 2P | 2 | [6 empty] | 3 | 0.05 | 0.1 | 0.15 | 0.34993 | 0.35137 | 0.8032
2P excitation frequency | f_2P | 0.4356 | Hz | [5 empty] | 4 | 0.066667 | 0.13333 | 0.2 | 0.34993 | 0.35137 | 0.8032
3P multiplier | 3P | 3 | [6 empty] | 5 | 0.083333 | 0.16667 | 0.25 | 0.34993 | 0.35137 | 0.8032
3P excitation frequency | f_3P | 0.65339 | Hz | [5 empty] | 6 | 0.1 | 0.2 | 0.3 | 0.34993 | 0.35137 | 0.8032
[9 empty] | 7 | 0.11667 | 0.23333 | 0.35 | 0.34993 | 0.35137 | 0.8032
where | [8 empty] | 8 | 0.13333 | 0.26667 | 0.4 | 0.34993 | 0.35137 | 0.8032
Blade flapwise vibration natural frequency | f_n | 0.34993 | Hz | [5 empty] | 9 | 0.15 | 0.3 | 0.45 | 0.34993 | 0.35137 | 0.8032
Frequency ratio, 1P | r_1P | 0.6224 | - | [5 empty] | 10 | 0.16667 | 0.33333 | 0.5 | 0.34993 | 0.35137 | 0.8032
Frequency ratio, 2P | r_2P | 1.2448 | - | [5 empty] | 11 | 0.18333 | 0.36667 | 0.55 | 0.34993 | 0.35137 | 0.8032
Frequency ratio, 3P | r_3P | 1.8672 | - | [5 empty] | 12 | 0.2 | 0.4 | 0.6 | 0.34993 | 0.35137 | 0.8032
[9 empty] | 13.0679 | 0.2178 | 0.4356 | 0.65339 | 0.34993 | 0.35137 | 0.8032
If damping is 0 then |  | No damping | Aerodynamic damping
|  | ζ=0 | ζ=0.15
0.15
Dynamic magnification factor, 1P | Q_1P | 1.6323 | 1.5614
Dynamic magnification factor, 2P | Q_2P | -1.8197 | 1.5051
Dynamic magnification factor, 3P | Q_3P | -0.40218 | 0.39234

## Generator design
| Direct Drive PMG |  | Comments
Rated power | 4500000 | W | 4.5MW
Gearbox ratio, k | 1 |  | gear ratios 1:1
Generator rotational speed | 13.1 | rpm
Generator rotational speed | 1.3718 | rad/s
Generator rated torque, T | 3280292.7202 | Nm
Generator "radius/axial length" ratio or R/L | 2 |  | Assume Kasp=2
Electromagnetic Shear Stress, σ | 40000 | Pa | Assume 40kPa
Generator radius, R | 2.9664 | m
Generator axial length, L | 1.4832 | m
Generator cylinder surface area, 2πRL | 27.6451 | m2 |  | (1$=0.8£, 1¥=0.12£ 13/4/2023 UTC 16:53)
Generator volume, V | 41.0037 | m3 |  | Commodities - Live Quote Price Trading Data (tradingeconomics.com)
|  |  |  | Parameter | Price |  | Price date | Price in £
Iron mass | 26.5458 | ton | Use Surface Area x "Mass/surface area" (from Polinder) | Iron mass price per tons | 116 | USD/tons | 21/4/2023 | 92.8 | £/tons
Copper mass | 6.3065 | ton |  | Copper mass price tons | 3.848 | USD/Lbs | 21/4/2023 | 6895.616 | £/tons
Permanent magnet mass | 2.4933 | ton |  | Neodymium（Permanent magnet） mass price per tons | 605000 | RMB/tons | 21/4/2023 | 72600 | £/tons
Pole pitch guess | 0.1 | m | 0.1m pole pitch is similar to Polinder | Cost
Poles guess | 186.3864 |  |  | Iron | 2463.4502 | £
Pole pairs guess | 93.1932 |  |  | Copper | 43486.9315 | £
|  |  |  | Permanent magnet | 181010.0892 | £
Integer pole pairs | 93 |  | Pole pairs must be integer, so round to nearest | Total Cost | 226960.471 | £
Integer poles | 186
Pole pitch | 0.10021 | m
Copper loss estimate | 36802.4946 | w | Estimate based on Surface Area x "loss/surface area"
Iron loss estimate | 21999.2816 | w
Total loss estimate | 58801.7763 | w
𝑃𝑜𝑙𝑒 𝑝𝑖𝑡𝑐ℎ= 2𝜋𝑅/𝑃𝑜𝑙𝑒𝑠
𝑇=𝜎2𝜋𝑅^2 𝐿
𝑇=𝜎2𝜋𝑅^3 (𝐿/𝑅)
𝑅=∛(𝑇/𝜎2𝜋(𝑅/𝐿))

## Foundation design
wind speed | thrust
m/s | kN
1 | 8.8652
2 | 30.6805
3 | 63.3409
4 | 96.8557
5 | 142.081
6 | 189.701
7 | 244.372
8 | 303.745
9 | 381.828
10 | 469.663
11 | 552.391
11.78 | 606.707
12 | 551.547
13 | 473.571
14 | 417.466
15 | 384.829
16 | 359.695
17 | 321.301
18 | 291.829
19 | 287.38
20 | 279.647
21 | 272.642
22 | 265.366
23 | 255.839
24 | 237.172
25 | 229.837
Rotor mass | 84.61 | t
Nacelle mass | 177.715 | t
Tower mass | 257.937 | t
Total mass | 520.262 | t |  | weight W of the tower+nacelle+roter | 5103770.22 | N
concrete plinth | 1.5 | m
buried depth | 1.8 | m
hub height | 79.252 | m
density of reinforced concrete | 2500 | kg/m3
density of the soil and rock backfill | 2200 | kg/m3
rotor thrust | 606.707 | kN
overturning moment is Mt | 50084.8763 | kNm | Mt=TH
concrete plinth and the overlying soil Mc | 3750 | B² kg
mass of soil Ms | 3960 | B² kg
The total mass of the base Mb | 7710 | B² kg
gravity g | 9.81 | m/s²
weight W of the foundation | 75635.1 | B² N
weight moment Mw | 37817.55 | B³ Nm | Mw=WB/2 | weight moment Mw' | 37817.55 | B³ ＋ | 2551885.11 | B | Nm
B | 15.8384 | m | Mw≥3Mt | B | 14.4224 |  |  |  | m | Mw'≥3Mt
[8 empty] | Calculation process |  | -1.2726e-05
cost
volume | 245.0508 | m³
steel bars needed | 40 | t | assumed
cost list
Concrete C40 price | 115 | £/m³ | Ready Mix Concrete Prices for 2023 ¦ Mister Concrete
steel bars | 461.76 | £/t
concrete | 28180.8372 | £
steel bars | 18470.4 | £
total | 46651.2372 | £

## Energy Yield
"V1" | "V2" | Rayleigh fit at 78.5m | Wind Speed (m) | Power (kW) | P90 Energy (kWh)
0 | 0.5 | 49.2701 | 0 | 0 | 0
0.5 | 1.5 | 384.3145 | 1 | 0 | 0
1.5 | 2.5 | 718.5097 | 2 | 0 | 0
2.5 | 3.5 | 963.2009 | 3 | 41.3979 | 39874.4936
3.5 | 4.5 | 1097.3009 | 4 | 170.099 | 186649.7856
4.5 | 5.5 | 1120.4255 | 5 | 343.608 | 384987.1492
5.5 | 6.5 | 1049.998 | 6 | 641.894 | 673987.3874
6.5 | 7.5 | 914.611 | 7 | 1034.53 | 946192.5262
7.5 | 8.5 | 746.1161 | 8 | 1556.85 | 1161590.8087
8.5 | 9.5 | 572.8141 | 9 | 2209.27 | 1265500.9351
9.5 | 10.5 | 415.2432 | 10 | 3029.67 | 1258049.8637
10.5 | 11.5 | 284.9069 | 11 | 4039.22 | 1150801.8464
11.5 | 12.5 | 185.3428 | 12 | 4841.82 | 897396.5219
12.5 | 13.5 | 114.4717 | 13 | 4909.54 | 562003.3858
13.5 | 14.5 | 67.1922 | 14 | 4854.33 | 326173.2562
14.5 | 15.5 | 37.5141 | 15 | 4894.49 | 183612.2802
15.5 | 16.5 | 19.9347 | 16 | 4846.33 | 96610.3243
16.5 | 17.5 | 10.0879 | 17 | 4864.93 | 49077.1093
17.5 | 18.5 | 4.8637 | 18 | 4981.15 | 24226.6607
18.5 | 19.5 | 2.2349 | 19 | 4968.14 | 11103.2898
19.5 | 20.5 | 0.97909 | 20 | 4867.98 | 4766.1798
20.5 | 21.5 | 0.40905 | 21 | 4898.2 | 2003.5914
21.5 | 22.5 | 0.16301 | 22 | 4978.85 | 811.5976
22.5 | 23.5 | 0.061976 | 23 | 4932.38 | 305.6911
23.5 | 24.5 | 0.022485 | 24 | 4917.32 | 110.5659
24.5 | 25.5 | 0.0077853 | 25 | 4995.86 | 38.8944
25.5 | 26.5 | 0.002573
26.5 | 27.5 | 0.00081177
27.5 | 28.5 | 0.00024451
28.5 | 29.5 | 7.0321e-05 | energy per WT per year |  | 9225874.1443
29.5 | 30.5 | 1.9312e-05 | energy 3 WTs per year |  | 27677622.433

## Controller Design
rated wind speed | 11.604 | m/s
K_u | 2.99 | s
T_u | 3.525 | s
K_p(0) | 1.3455 | s
K_I(0) | 0.45804
theta_k | 40 | degrees

## Curves
calculated value
rated power | 4500000 | w | decided
cut wind | 3 | m/s
rated wind | 11.7831 | m/s
cut out | 25 | m/s
Diameter | 113.9965 | m
radio | 56.9982 | m
sweatp area | 10206.4061 | m2 | calculated
max tip speed | 78 | m/s
Specific power | 440.8996 | w/m2 | calculated
hub height | 79.252
rho | 1.225 | kg/m^3
Cp | 0.48892
Tip speed ratio at rated | 6.6196 |  | calculated
Rated rotor speed | 1.3685 | rad/s | calculated
calculated value
wind speed | P in wind | P_max | P_generated | P_generated | Cp | Tip speed ratio | Rotor speed (rad/s) | Rotor speed (rpm) | Torque (kNm)
m/s | W | W | W | kW | % |  | rad/s | rpm | kNm
0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
3 | 168788.4402 | 82524.5505 | 82524.5505 | 82.5246 | 0.48892 | 6.6196 | 0.34841 | 3.3271 | 236.8586
4 | 400091.1174 | 195613.7494 | 195613.7494 | 195.6137 | 0.48892 | 6.6196 | 0.46455 | 4.4361 | 421.0819
5 | 781427.9637 | 382058.1043 | 382058.1043 | 382.0581 | 0.48892 | 6.6196 | 0.58069 | 5.5452 | 657.9405
6 | 1350307.5212 | 660196.4042 | 660196.4042 | 660.1964 | 0.48892 | 6.6196 | 0.69683 | 6.6542 | 947.4343
7 | 2144238.3323 | 1048367.4381 | 1048367.4381 | 1048.3674 | 0.48892 | 6.6196 | 0.81296 | 7.7632 | 1289.5633
8 | 3200728.9392 | 1564909.9951 | 1564909.9951 | 1564.91 | 0.48892 | 6.6196 | 0.9291 | 8.8723 | 1684.3276
9 | 4557287.8841 | 2228162.8642 | 2228162.8642 | 2228.1629 | 0.48892 | 6.6196 | 1.0452 | 9.9813 | 2131.7271
10 | 6251423.7093 | 3056464.8342 | 3056464.8342 | 3056.4648 | 0.48892 | 6.6196 | 1.1614 | 11.0903 | 2631.7618
11 | 8320644.9571 | 4068154.6944 | 4068154.6944 | 4068.1547 | 0.48892 | 6.6196 | 1.2775 | 12.1994 | 3184.4318
11.7831 | 10227272.7273 | 5000348.8636 | 4500000 | 4500 | 0.44 | 6.6196 | 1.3685 | 13.0679 | 3288.3603
12 | 10802460.1697 | 5281571.2336 | 4500000 | 4500 | 0.41657 | 6.5 | 1.3685 | 13.0679 | 3288.3603
13 | 13734377.8894 | 6715053.2408 | 4500000 | 4500 | 0.32764 | 6 | 1.3685 | 13.0679 | 3288.3603
14 | 17153906.6584 | 8386939.5051 | 4500000 | 4500 | 0.26233 | 5.5714 | 1.3685 | 13.0679 | 3288.3603
15 | 21098555.019 | 10315568.8155 | 4500000 | 4500 | 0.21328 | 5.2 | 1.3685 | 13.0679 | 3288.3603
16 | 25605831.5134 | 12519279.961 | 4500000 | 4500 | 0.17574 | 4.875 | 1.3685 | 13.0679 | 3288.3603
17 | 30713244.6839 | 15016411.7306 | 4500000 | 4500 | 0.14652 | 4.5882 | 1.3685 | 13.0679 | 3288.3603
18 | 36458303.0728 | 17825302.9133 | 4500000 | 4500 | 0.12343 | 4.3333 | 1.3685 | 13.0679 | 3288.3603
19 | 42878515.2223 | 20964292.298 | 4500000 | 4500 | 0.10495 | 4.1053 | 1.3685 | 13.0679 | 3288.3603
20 | 50011389.6746 | 24451718.6739 | 4500000 | 4500 | 0.08998 | 3.9 | 1.3685 | 13.0679 | 3288.3603
21 | 57894434.9721 | 28305920.8298 | 4500000 | 4500 | 0.077728 | 3.7143 | 1.3685 | 13.0679 | 3288.3603
22 | 66565159.6569 | 32545237.5549 | 4500000 | 4500 | 0.067603 | 3.5455 | 1.3685 | 13.0679 | 3288.3603
23 | 76061072.2714 | 37188007.6381 | 4500000 | 4500 | 0.059163 | 3.3913 | 1.3685 | 13.0679 | 3288.3603
24 | 86419681.3577 | 42252569.8685 | 4500000 | 4500 | 0.052071 | 3.25 | 1.3685 | 13.0679 | 3288.3603
25 | 97678495.4582 | 47757263.0349 | 4500000 | 4500 | 0.04607 | 3.12 | 1.3685 | 13.0679 | 3288.3603
measured value
Wind Speed | P_generated | Rotational Speed | Rotational speed | Pitch Angle | Torque | Cp | P_max
m/s | kW | rpm | rad/s | ° | kNm |  | kW
0 | 0 | 0 | 0 | 0 | 0
1 | 0 | 0 | 0 | 0 | 0 | 0.0052613
2 | 0 | 0 | 0 | 0 | 0 | 0.02295
3 | 41.3979 | 7.5403 | 0.78962 | 0 | 52.4278 | 0.10174 | 105.276
4 | 170.099 | 7.7583 | 0.81245 | 0 | 209.366 | 0.21496 | 221.447
5 | 343.608 | 8.0886 | 0.84704 | 0 | 405.659 | 0.355 | 429.987
6 | 641.894 | 8.5201 | 0.89222 | 0 | 719.436 | 0.44123 | 737.025
7 | 1034.53 | 9.034 | 0.94604 | 0 | 1093.55 | 0.47943 | 1122.61
8 | 1556.85 | 9.6499 | 1.0105 | 0 | 1540.61 | 0.48889 | 1640.93
9 | 2209.27 | 10.7911 | 1.13 | 0 | 1955.03 | 0.48379 | 2313.92
10 | 3029.67 | 11.9864 | 1.2552 | 0 | 2413.67 | 0.46626 | 3177.81
11 | 4039.22 | 12.7878 | 1.3391 | 0 | 3016.29 | 0.438 | 4209.25
11.8 | 4831.93 | 12.9622 | 1.3574 | 0 | 3559.71 | 0.40803 | 4944.24
12 | 4841.82 | 13.0993 | 1.3718 | 1.8085 | 3529.66 | 0.39955 | 5995.66
13 | 4909.54 | 13.1068 | 1.3725 | 5.2931 | 3576.98 | 0.35202 | 6095.25
14 | 4854.33 | 13.1141 | 1.3733 | 7.6629 | 3534.77 | 0.29626 | 6095.25
15 | 4894.49 | 13.1089 | 1.3728 | 9.6111 | 3565.43 | 0.2327 | 6288.04
16 | 4846.33 | 13.0967 | 1.3715 | 11.3508 | 3533.63 | 0.16049 | 6324.69
17 | 4864.93 | 13.0838 | 1.3701 | 12.9207 | 3550.7 | 0.079153 | 6324.69
18 | 4981.15 | 13.1122 | 1.3731 | 14.3909 | 3627.64 |  | 6324.69
19 | 4968.14 | 13.1081 | 1.3727 | 15.7901 | 3619.3 |  | 6324.69
20 | 4867.98 | 13.0798 | 1.3697 | 17.1362 | 3554 |  | 6612.25
21 | 4898.2 | 13.0759 | 1.3693 | 18.6906 | 3577.14 |  | 6612.25
22 | 4978.85 | 13.0811 | 1.3698 | 19.6066 | 3634.58 |  | 6652.15
23 | 4932.38 | 13.0744 | 1.3691 | 20.7945 | 3602.51 |  | 6749.92
24 | 4917.32 | 13.0702 | 1.3687 | 21.9005 | 3592.68 |  | 6792.8
25 | 4995.86 | 13.0848 | 1.3702 | 23.0237 | 3645.99 |  | 6801.38
𝑃=□(64&1/2)𝑐_𝑃 𝜌𝐴𝑈^3
𝑆𝑝𝑒𝑐𝑖𝑓𝑖𝑐 𝑃𝑜𝑤𝑒𝑟=𝑃𝑜𝑤𝑒𝑟/(𝑆𝑤𝑒𝑝𝑡 𝐴𝑟𝑒𝑎)

## Cost
WT P_r | 4500 | kW
Averaged CapEx | 1501 | $/kW
Parameter | Value | Cost | Cost |  | 2021 Cost of Wind Energy Review (nrel.gov)
| $/kW | $ | £
Wind Turbine CapEx | 1030 | 1546030 | 1236824
Rotor | 313 | 469813 | 375850.4
Nacelle | 512 | 768512 | 614809.6
Tower | 204 | 306204 | 244963.2
Bos CapEx | 322 | 483322 | 386657.6
Engineering | 23 | 34523 | 27618.4
Project Management | 10 | 15010 | 12008
Foundation | 75 | 112575 | 90060
Site access, staing, facilities | 40 | 60040 | 48032
Assembly and installation | 41 | 61541 | 49232.8
Electrical infrastructure | 132 | 198132 | 158505.6
Financial CapEx | 113 | 169613 | 135690.4
Construction finance | 23 | 34523 | 27618.4
Contingency | 90 | 135090 | 108072
Total CapEx | 1501 | 2253001 | 1802400.8
(1$=0.8£, 13/4/2023 UTC 16:53)
Annual cost (fixed)
Insurance and taxes | 38000 | £ | tutorial
Electrical O&M | 3000 | £ | tutorial
Management | 8000 | £ | tutorial
Annual costs (variable) |  |  | tutorial
Availability warranty | 13.5705 | £/MWh | scale 15 to factor of 0.9047
Estimated OpEx | 32 | £/kW-yr
Estimated Total OpEx | 144000 | £/yr
Assuming a 20-year lifetime
life time | 20 | year
discount rate | 1.3 | % | https://www.gov.uk/government/publications/dhsc-group-accounting-manual-2021-to-2022/department-of-health-and-social-care-group-accounting-manual-2021-to-2022-additional-guidance-version-1#:~:text=Post%2Demployment%20benefits%20provisions,of%20CPI%20measured%20at%202.90%25.
Annual energy yield | 9225.8741 | MWh
Total capital costs C | 1802400.8 | £
Total fixed costs | 49000 | £
Annual cost per unit output O | 18.8816 | £/MWh
Discounting factor S_n | 17.7396
LCoE | 29.8945 | £/MWh
How much does a wind turbine cost ? - Renewables First
Maximum Power Output (kW) | Typical Turbine Type | Project Cost |  | actual cost around
100 | Norvento nED100 | 405 | k£ | 279450 | £
800 | Enercon E53 | 1030 | k£ | 710700 | £
1000 | EWT DW61 | 1250 | k£ | 862500 | £
3000 | Enercon E82 | 2330 | k£ | 1607700 | £
3500 | Enercon E126 EP3 | 3130 | k£ | 2159700 | £
estimate for 4500 |  |  |  | 2535728 | £
𝐿𝐶𝑜𝐸=𝐶/(𝑆_𝑛 𝐸)+𝑂
𝑆_𝑛=1+1/𝑟[1−(1+𝑟)^(1−𝑛)]

## WT Scale
P_r | 4500000 | W
v_r | 11.7831 | m/s
rho | 1.225 | kg/m^3
c_p_max | 0.44 |  | guess （Borrowed from Enercon E-112/45.114）
New rotor radius | 56.9982 | m
Original rotor radius | 63 | m
Scale factor | 0.90473
Original hub radius | 1.5 | m
New hub radius | 1.3571 | m
Original blade length | 61.5 | m
New blade length | 55.6411 | m

## cp-lambda data from Ashes
TSR | Cp | Ct
1 | 0.0052613 | 0.078909 | cp_max | 0.48892
1.1 | 0.0059704 | 0.081711 | lambda_optimal | 8.1
1.2 | 0.0067232 | 0.084662
1.3 | 0.0075297 | 0.087736
1.4 | 0.0084313 | 0.090997
1.5 | 0.0095485 | 0.094575
1.6 | 0.011041 | 0.098635
1.7 | 0.01306 | 0.10333
1.8 | 0.015699 | 0.10878
1.9 | 0.018999 | 0.11503
2 | 0.02295 | 0.12206
2.1 | 0.027627 | 0.12995
2.2 | 0.033129 | 0.13872
2.3 | 0.039562 | 0.14844
2.4 | 0.046882 | 0.15899
2.5 | 0.054889 | 0.17014
2.6 | 0.063545 | 0.18178
2.7 | 0.072629 | 0.19368
2.8 | 0.08209 | 0.20576
2.9 | 0.091827 | 0.21795
3 | 0.10174 | 0.23017
3.1 | 0.11186 | 0.24246
3.2 | 0.12211 | 0.25476
3.3 | 0.13256 | 0.26715
3.4 | 0.14338 | 0.27985
3.5 | 0.15459 | 0.2928
3.6 | 0.16614 | 0.30595
3.7 | 0.17793 | 0.31916
3.8 | 0.18996 | 0.33239
3.9 | 0.20227 | 0.3457
4 | 0.21496 | 0.35915
4.1 | 0.22799 | 0.37263
4.2 | 0.24149 | 0.38625
4.3 | 0.25525 | 0.3999
4.4 | 0.26937 | 0.4137
4.5 | 0.28376 | 0.42773
4.6 | 0.29807 | 0.44188
4.7 | 0.31237 | 0.4567
4.8 | 0.32612 | 0.47224
4.9 | 0.3403 | 0.48967
5 | 0.355 | 0.50892
5.1 | 0.36887 | 0.52801
5.2 | 0.38233 | 0.54691
5.3 | 0.39364 | 0.56354
5.4 | 0.4039 | 0.57921
5.5 | 0.41189 | 0.59268
5.6 | 0.41884 | 0.60516
5.7 | 0.425 | 0.61699
5.8 | 0.43067 | 0.6284
5.9 | 0.43608 | 0.63953
6 | 0.44123 | 0.65035
6.1 | 0.44605 | 0.66082
6.2 | 0.45062 | 0.67099
6.3 | 0.45491 | 0.68089
6.4 | 0.45894 | 0.69042
6.5 | 0.46284 | 0.69961
6.6 | 0.46658 | 0.7084
6.7 | 0.47015 | 0.717
6.8 | 0.47352 | 0.72545
6.9 | 0.47666 | 0.73377
7 | 0.47943 | 0.74185
7.1 | 0.48165 | 0.7495
7.2 | 0.48327 | 0.75679
7.3 | 0.48454 | 0.76379
7.4 | 0.48563 | 0.77067
7.5 | 0.48653 | 0.77739
7.6 | 0.4873 | 0.78396
7.7 | 0.4879 | 0.79033
7.8 | 0.48837 | 0.79655
7.9 | 0.48869 | 0.80268
8 | 0.48889 | 0.80876
8.1 | 0.48892 | 0.81474
8.2 | 0.48883 | 0.82064
8.3 | 0.48863 | 0.8265
8.4 | 0.48832 | 0.8323
8.5 | 0.48789 | 0.83804
8.6 | 0.48733 | 0.8437
8.7 | 0.48665 | 0.84929
8.8 | 0.48583 | 0.8548
8.9 | 0.48488 | 0.86022
9 | 0.48379 | 0.86557
9.1 | 0.48258 | 0.87085
9.2 | 0.48124 | 0.87607
9.3 | 0.47977 | 0.88123
9.4 | 0.47817 | 0.88633
9.5 | 0.47645 | 0.89138
9.6 | 0.47462 | 0.89638
9.7 | 0.47269 | 0.90133
9.8 | 0.47065 | 0.90622
9.9 | 0.46851 | 0.91106
10 | 0.46626 | 0.91583
10.1 | 0.46392 | 0.92054
10.2 | 0.46146 | 0.92519
10.3 | 0.4589 | 0.92977
10.4 | 0.45623 | 0.93429
10.5 | 0.45346 | 0.93877
10.6 | 0.45058 | 0.9432
10.7 | 0.44759 | 0.94758
10.8 | 0.44449 | 0.95192
10.9 | 0.44129 | 0.95622
11 | 0.438 | 0.96047
11.1 | 0.4346 | 0.96467
11.2 | 0.43111 | 0.96883
11.3 | 0.42751 | 0.97294
11.4 | 0.42381 | 0.97699
11.5 | 0.42002 | 0.98099
11.6 | 0.41613 | 0.98494
11.7 | 0.41213 | 0.98885
11.8 | 0.40803 | 0.99271
11.9 | 0.40383 | 0.99653
12 | 0.39955 | 1.0003
12.1 | 0.39517 | 1.0041
12.2 | 0.39071 | 1.0078
12.3 | 0.38616 | 1.0115
12.4 | 0.38152 | 1.0152
12.5 | 0.3768 | 1.0188
12.6 | 0.372 | 1.0224
12.7 | 0.36713 | 1.026
12.8 | 0.36218 | 1.0295
12.9 | 0.35714 | 1.0331
13 | 0.35202 | 1.0366
13.1 | 0.34681 | 1.04
13.2 | 0.34152 | 1.0435
13.3 | 0.33614 | 1.0469
13.4 | 0.33069 | 1.0503
13.5 | 0.32515 | 1.0537
13.6 | 0.31952 | 1.057
13.7 | 0.31382 | 1.0604
13.8 | 0.30805 | 1.0637
13.9 | 0.30219 | 1.067
14 | 0.29626 | 1.0703
14.1 | 0.29025 | 1.0736
14.2 | 0.28417 | 1.0768
14.3 | 0.27801 | 1.0801
14.4 | 0.27177 | 1.0833
14.5 | 0.26546 | 1.0865
14.6 | 0.25908 | 1.0897
14.7 | 0.25261 | 1.093
14.8 | 0.24606 | 1.0962
14.9 | 0.23941 | 1.0993
15 | 0.2327 | 1.1025
15.1 | 0.22589 | 1.1057
15.2 | 0.21899 | 1.1088
15.3 | 0.21199 | 1.112
15.4 | 0.20489 | 1.1151
15.5 | 0.19771 | 1.1182
15.6 | 0.19044 | 1.1214
15.7 | 0.18308 | 1.1245
15.8 | 0.17564 | 1.1276
15.9 | 0.16811 | 1.1307
16 | 0.16049 | 1.1338
16.1 | 0.15279 | 1.1369
16.2 | 0.14501 | 1.14
16.3 | 0.13712 | 1.1431
16.4 | 0.12912 | 1.1462
16.5 | 0.12103 | 1.1493
16.6 | 0.11286 | 1.1523
16.7 | 0.10458 | 1.1554
16.8 | 0.096201 | 1.1585
16.9 | 0.087725 | 1.1615
17 | 0.079153 | 1.1646
17 | 0.079153 | 1.1646

## Rotor Scale
Maximum tip speed | 78 | m/s
Rotor radius | 56.9982 | m
Maximum rotational speed | 1.3685 | rad/s
Maximum rpm | 13.0679 | rpm
Maximum c_p | 0.48892
Optimal tip speed ratio | 8.1
v_r | 11.7831 | m/s
Optimal rotor rpm at rated | 15.9902 | rpm

## 3MW-DDPMG
| Direct Drive PMG |  |  | Paper
Rated power | 3000000 | W | Table 1 | IEEE TRANSACTIONS ON ENERGY CONVERSION, VOL. 21, NO. 3, SEPTEMBER 2006 725 Comparison of Direct-Drive and Geared Generator Concepts for Wind Turbines
Rotational speed | 15 | rpm | Table 1 | Digital Object Identifier 10.1109/TEC.2006.875476 | https://ieeexplore.ieee.org/document/1677663 | Polinder et al.
Rotational speed | 1.5708 | rad/s
Rated torque, T | 1909859.3171 | Nm
Generator radius, R | 2.5 | m | Table 2
Generator axial length, L | 1.2 | m | Table 2
Generator "radius/axial length" ratio or R/L | 2.0833 | -
Electromagnetic Shear Force, F | 763943.7268 | N
Generator cylinder surface area, 2πRL | 18.8496 | m^2
Electromagnetic Shear Stress, σ | 40528.4735 | Pa
Iron mass | 18.1 | ton | Table 2
Copper mass | 4.3 | ton | Table 2
Permanent magnt mass | 1.7 | ton | Table 2
Iron mass/area | 0.96023 | ton/m2
Copper mass/area | 0.22812 | ton/m2
Permanent magnet mass/area | 0.090188 | ton/m2
Pole pairs | 80 | - | Table 2
Poles | 160 | -
Pole pitch | 0.098175 | m
Rated iron losses | 15000 | W
Rated copper losses | 110000 | W
Iron losses per area | 795.7747 | W/m2
Copper losses per area | 5835.6812 | W/m2
Losses per area | 6631.456 | W/m2